## DR Program List
Program Category | Program Option | Electric DR (WA, ID) | Electric DR- Ancillary Services | Gas DR (WA, ID, OR) | Mechanism/Notes | Residential | General Service | Large General Service | Extra Large General Service
Conventional DLC | DLC Central AC | ü |  |  | DLC switch installed on Central AC compressor (Start 1/2024) | ü | ü
| DLC Water Heating | ü | ü | ü | DLC switch installed on customer’s Water Heater (Idho Only) | ü | ü
| DLC Electric Vehicle Charging | ü | ü |  | DLC switch installed on customer’s equipment | ü
Smart/ Interactive DLC | DLC Smart Thermostats - Cooling | ü | ü |  | Internet-enabled control of thermostat set points, can be coupled with any dynamic pricing rate. BYOT and API integrations (Start 1/2024) | ü | ü
| DLC Smart Thermostats - Heating | ü | ü | ü | Internet-enabled control of thermostat set points, can be coupled with any dynamic pricing rate. BYOT and API integrations (Start 12/2024) Furnaces and Heat Pumps as end use tech. | ü | ü
| V1G EV Charging | ü | ü |  | Charging of Evs on program are controlled and adjusted by the utility or grid operator. Vehicle cannot discharge back to the grid. Control is one-way from the grid to the vehicle | ü
| Grid-Interactive WH (CTA-2045) | ü | ü | ü | Modular communications interface for water heaters that will become the new technology standard. Washington only (Start 1/2024). | ü | ü
| DLC Smart Appliances | ü | ü |  | Internet-enabled control of operational cycles of white goods appliances | ü | ü
Curtailment | Capacity Bidding (Third Party) | ü | ü | ü | Customers volunteer a specified amount of capacity (firm curtailment) during a predefined “economic event” called by the utility in return for a financial incentive. AEG uses this as a benchmark for smaller General Service customers. |  | ü |  |  | $50/kW might be too low to convince shedding
| Emergency Curtailment (Third Party) | ü | ü | ü | Customers enact their customized, mandatory curtailment plan. May use stand-by generation. Penalties apply for non-performance. For Gas, this would be the curtailment of non-essential process loads during DR events such as heating loads etc. |  |  | ü | ü | LDCs providing Nat gas programs - NW natural gas,
Energy Storage | Thermal Energy Storage | ü |  |  | Peak shifting of primarily space cooling or heating loads using a thermal storage medium such as water or ice |  | ü | ü | ü
| Battery Energy Storage | ü | ü |  | Peak shifting of loads using stored electrochemical energy | ü | ü | ü | ü
Time-Varying Rates/ Behavioral | Behavioral | ü |  | ü | Voluntary DR reductions in response to behavioral messaging. Example programs exist in CA and other states. Requires AMI technology. | ü
| Time-of-Use Opt-in | ü |  | ü | Higher rate for a particular block of hours that occurs every day. Requires either on/off peak meters or AMI technology. | ü | ü | ü | ü
| Time-of-Use Opt-out | ü |  | ü | Higher rate for a particular block of hours that occurs every day. Requires either on/off peak meters or AMI technology. | ü | ü | ü | ü
| Electric Vehicle Time-of-Use Opt-in | ü |  |  | Schedules 13 and 23. C&I EV TOU Rates. Washington only. Utilize EV forecast to update DR potential |  | ü | ü
| Peak Time Rebate | ü |  |  | The Peak Time Rebate (PTR) program offers participants an incentive for every kW saved during designated times of high energy demand. Events are called several times per season, and participants are given incentives in the form of $/kWh saved during the event relative to their baseline usage across previous seasons.
| Variable Peak Pricing Rates | ü |  | ü | Much higher rate for a particular block of hours that occurs only on event days. Requires AMI technology. | ü | ü | ü | ü
Used in Previous Study
Note on C8: Williams, Tommy: Pilot offering started in 2024
Note on E14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: New York tried a Behavioral DR program for Gas- no impacts, but a 30% participation rate (email openings)
Note on C15: Williams, Tommy: Pilot offering in 2024
Note on C19: Williams, Tommy: Pilot offering in 2024

## Current and Pilot Programs
Program Offering | Start Date | Classes | Program Details | Notes | (Ramp rates, expected participation, impacts per customer)
EV TOU | Current Program | GS, LGS | limited marketing and is currently being utilized by a few companies totaling five vehicles | Any new studies/findings on impacts or costs? | Five customers but more than five vehicles- these would just be vehicle loads
EVSE | Current Program | Res, GS, LGS | Avista currently has an Electric Vehicle Supply Equipment (EVSE) program in place for residential, commercial electric vehicle fleets, and workplace charging locations. AEG used the most recent per-customer program impacts from the EVSE program results for the study, assuming that, on average, 75% of electric vehicle load could be curtailed. Avista requested that this program be viewed as a fully-fledged program starting in 2024 to reflect the technology rollout. An EVSE rebate will be incentivized at a cost of $500 to Avista. An electric vehicle forecast was provided to AEG and provided the basis for estimating per-customer EV loads for this program, as well as the number of customers who could participate in an electric vehicle program. | Any new studies/findings on impacts or costs? | Leona will check in with EV team- also has a new program that involves incentive
Peak Time Rebate | 2024-06-01 | All classes | Service Agreement Adder- schedule 84 | expected participation/ ramp period? 15% SS | Limited participation and expected to run for two years | End date June 1 2026 | End enrollments june 1 2025 | begin ramp up in 2027 to fully-fledged program
TOU Opt-in | 2024-06-01 | Res, GS | Washington-only (schedule 7,8 for res and 17,18 for GS) | expected participation/ ramp period? 13% SS | Limited participation and expected to run for two years | End date June 1 2026 | End enrollments june 1 2025 | begin ramp up in 2027 to fully-fledged program
Grid Interactive WH | 2026? | Res, GS | NEEA partnered program to be added at later date | expected participation/ ramp period? 50% SS

## ParticipationRate
Key | State | Customer Class | Option | Data Element | Unit | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21 | Year 22 | Year 23 | Year 24 | Year 25 | Comments from Input Generator | Copy & Paste Values to Left into Model | Steady State Participation Rate | Program ramp up period | Program Dropout Rate (Attrition) | SS Partic Rate - Row Lookup | Ramp Up Yrs - Row Lookup | Column Lookup | Attrition Look Up - Row Look up | Note that Attrition will default to Low Participation Case since it is not differentiated by Case in the model.
WAResidentialDLC Central ACMarket Potential | WA | Residential | DLC Central AC | Market Potential | % of Eligible Customers | 1% | 3% | 7% | 9% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | NWPC DLC Switch cooling assumption- 5 yr ramp rate |  | 10% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAResidentialDLC Central ACProgram Dropout Rate (Attrition) | WA | Residential | DLC Central AC | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | NWPC DLC Switch cooling assumption- 5 yr ramp rate |  | 10% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAGeneral ServiceDLC Central ACMarket Potential | WA | General Service | DLC Central AC | Market Potential | % of Eligible Customers | 1% | 3% | 7% | 9% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | NWPC DLC Switch cooling assumption- 5 yr ramp rate |  | 10% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServiceDLC Central ACProgram Dropout Rate (Attrition) | WA | General Service | DLC Central AC | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | NWPC DLC Switch cooling assumption- 5 yr ramp rate |  | 10% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAResidentialDLC Smart Thermostats - CoolingMarket Potential | WA | Residential | DLC Smart Thermostats - Cooling | Market Potential | % of Eligible Customers | 2% | 6% | 14% | 18% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | NWPC Smart Thermostat cooling assumption- 5 yr ramp rate |  | 20% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition) |  | % of Steady State Participation
WAResidentialDLC Smart Thermostats - CoolingProgram Dropout Rate (Attrition) | WA | Residential | DLC Smart Thermostats - Cooling | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | NWPC Smart Thermostat cooling assumption- 5 yr ramp rate |  | 20% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition) |  |  |  |  | Program Years within Ramp Up (will slide with program start date) --->
WAGeneral ServiceDLC Smart Thermostats - CoolingMarket Potential | WA | General Service | DLC Smart Thermostats - Cooling | Market Potential | % of Eligible Customers | 1% | 3% | 7% | 9% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 2024 Avista Update |  | 10% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition) |  |  |  | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21 | Year 22 | Year 23 | Year 24 | Year 25
WAGeneral ServiceDLC Smart Thermostats - CoolingProgram Dropout Rate (Attrition) | WA | General Service | DLC Smart Thermostats - Cooling | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2024 Avista Update |  | 10% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition) |  | Total Ramp Up Years | 1 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAResidentialAncillary CoolingMarket Potential | WA | Residential | Ancillary Cooling | Market Potential | % of Eligible Customers | 1% | 3% | 7% | 9% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | Half of Thermostat Participation given an additional $20 as incentive |  | 10% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition) |  |  | 2 | 70% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAResidentialAncillary CoolingProgram Dropout Rate (Attrition) | WA | Residential | Ancillary Cooling | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Half of Thermostat Participation given an additional $20 as incentive |  | 10% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition) |  |  | 3 | 50% | 80% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAGeneral ServiceAncillary CoolingMarket Potential | WA | General Service | Ancillary Cooling | Market Potential | % of Eligible Customers | 1% | 3% | 7% | 9% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | NWPC Smart Thermostat cooling assumption- 5 yr ramp rate- Half for Ancillary |  | 10% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition) |  |  | 4 | 25% | 50% | 85% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAGeneral ServiceAncillary CoolingProgram Dropout Rate (Attrition) | WA | General Service | Ancillary Cooling | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | NWPC Smart Thermostat cooling assumption- 5 yr ramp rate- Half for Ancillary |  | 10% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition) |  |  | 5 | 10% | 30% | 70% | 90% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAResidentialDLC Smart Thermostats - HeatingMarket Potential | WA | Residential | DLC Smart Thermostats - Heating | Market Potential | % of Eligible Customers | 0.5% | 1.5% | 3.5% | 4.5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | Assuming maximum participation for combined DLC Cooling and Smart Therm is 25%, reduced from 30% to account for those program participants who may have intended to participate but were unable to correctly install their thermostat |  | 5% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition) |  |  | 6 | [5 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAResidentialDLC Smart Thermostats - HeatingProgram Dropout Rate (Attrition) | WA | Residential | DLC Smart Thermostats - Heating | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Assuming maximum participation for combined DLC Cooling and Smart Therm is 25%, reduced from 30% to account for those program participants who may have intended to participate but were unable to correctly install their thermostat |  | 5% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition) |  |  | 7 | 8% | 18% | 30% | 46% | 62% | 80% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAGeneral ServiceDLC Smart Thermostats - HeatingMarket Potential | WA | General Service | DLC Smart Thermostats - Heating | Market Potential | % of Eligible Customers | 0.3% | 0.9% | 2.1% | 2.7% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | Dropping to 3% to compensate for higher space heating saturations |  | 3% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition) |  |  | 8 | [7 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAGeneral ServiceDLC Smart Thermostats - HeatingProgram Dropout Rate (Attrition) | WA | General Service | DLC Smart Thermostats - Heating | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Dropping to 3% to compensate for higher space heating saturations |  | 3% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition) |  |  | 9 | [8 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAResidentialDLC Water HeatingMarket Potential | WA | Residential | DLC Water Heating | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Ensure population applies to the subset of customers participating in AC or Space Heating DLC- 25% max using studies from PLMA, BGE, and Brattle |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition) |  |  | 10 | 4% | 10% | 18% | 26% | 36% | 46% | 59% | 72% | 85% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAResidentialDLC Water HeatingProgram Dropout Rate (Attrition) | WA | Residential | DLC Water Heating | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Ensure population applies to the subset of customers participating in AC or Space Heating DLC- 25% max using studies from PLMA, BGE, and Brattle |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition) |  |  | 11 | 14% | 19% | 26% | 33% | 42% | 51% | 63% | 75% | 87% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAGeneral ServiceDLC Water HeatingMarket Potential | WA | General Service | DLC Water Heating | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | * Changed from 3% to reflect a Brattle Study to the left that estimates 5-10% |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition) |  |  | 12 | [11 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAGeneral ServiceDLC Water HeatingProgram Dropout Rate (Attrition) | WA | General Service | DLC Water Heating | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | * Changed from 3% to reflect a Brattle Study to the left that estimates 5-10% |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition) |  |  | 13 | [12 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAResidentialAncillary DLC WHMarket Potential | WA | Residential | Ancillary DLC WH | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Ensure population applies to the subset of customers participating in AC or Space Heating DLC |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition) |  |  | 14 | 2% | 6% | 10% | 16% | 22% | 28% | 34% | 42% | 50% | 58% | 68% | 78% | 88% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAResidentialAncillary DLC WHProgram Dropout Rate (Attrition) | WA | Residential | Ancillary DLC WH | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Ensure population applies to the subset of customers participating in AC or Space Heating DLC |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition) |  |  | 15 | 2% | 4% | 8% | 12% | 16% | 22% | 28% | 34% | 42% | 50% | 58% | 68% | 78% | 88% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAGeneral ServiceAncillary DLC WHMarket Potential | WA | General Service | Ancillary DLC WH | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | * Changed from 3% to reflect a Brattle Study to the left that estimates 5-10% |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition) |  |  | 16 | [15 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAGeneral ServiceAncillary DLC WHProgram Dropout Rate (Attrition) | WA | General Service | Ancillary DLC WH | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | * Changed from 3% to reflect a Brattle Study to the left that estimates 5-10% |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition) |  |  | 17 | [16 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAResidentialAncillary HeatingMarket Potential | WA | Residential | Ancillary Heating | Market Potential | % of Eligible Customers | 0.25% | 0.75% | 1.75% | 2.25% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | Half for ancillary |  | 2.5% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition) |  |  | 18 | [17 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAResidentialAncillary HeatingProgram Dropout Rate (Attrition) | WA | Residential | Ancillary Heating | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Half for ancillary |  | 2.5% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition) |  |  | 19 | [18 empty] | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAGeneral ServiceAncillary HeatingMarket Potential | WA | General Service | Ancillary Heating | Market Potential | % of Eligible Customers | 0.15% | 0.45% | 1.05% | 1.35% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | Dropping to 3% to compensate for higher space heating saturations- half for ancillary |  | 1.5% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition) |  |  | 20 | 1% | 3% | 5% | 7% | 11% | 15% | 19% | 23% | 27% | 31% | 35% | 39% | 43% | 51% | 59% | 67% | 75% | 83% | 91% | 100% | 100% | 100% | 100% | 100% | 100%
WAGeneral ServiceAncillary HeatingProgram Dropout Rate (Attrition) | WA | General Service | Ancillary Heating | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Dropping to 3% to compensate for higher space heating saturations- half for ancillary |  | 1.5% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition) |  |  | 21 | [20 empty] | 100% | 100% | 100% | 100% | 100%
WAResidentialPilot-CTA-2045 HPWHMarket Potential | WA | Residential | Pilot-CTA-2045 HPWH | Market Potential | % of Eligible Customers | 0.8% | 1.28% | 1.6% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 1.6% | 3.5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition) |  |  | 3.5 | 50% | 80% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
WAResidentialPilot-CTA-2045 HPWHProgram Dropout Rate (Attrition) | WA | Residential | Pilot-CTA-2045 HPWH | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Modified to reflect pilot scope |  | 1.6% | 3.5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition) |  |  | 5.5 | 100% | 100% | 100% | 100% | 100% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
WAGeneral ServicePilot-CTA-2045 HPWHMarket Potential | WA | General Service | Pilot-CTA-2045 HPWH | Market Potential | % of Eligible Customers | 0.75% | 1.2% | 1.5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 1.5% | 3.5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition) |  |  | 0 | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
WAGeneral ServicePilot-CTA-2045 HPWHProgram Dropout Rate (Attrition) | WA | General Service | Pilot-CTA-2045 HPWH | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Modified to reflect pilot scope |  | 1.5% | 3.5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAResidentialPilot-Ancillary HPWHMarket Potential | WA | Residential | Pilot-Ancillary HPWH | Market Potential | % of Eligible Customers | 0.8% | 1.28% | 1.6% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 1.6% | 3.5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAResidentialPilot-Ancillary HPWHProgram Dropout Rate (Attrition) | WA | Residential | Pilot-Ancillary HPWH | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Modified to reflect pilot scope |  | 1.6% | 3.5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition) |  |  | 5 Year |  | 10% | 12% | 16% | 16% | 18% | 20%
WAGeneral ServicePilot-Ancillary HPWHMarket Potential | WA | General Service | Pilot-Ancillary HPWH | Market Potential | % of Eligible Customers | 0.75% | 1.2% | 1.5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 1.5% | 3.5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition) |  |  | 10 Year |  | 6% | 8% | 8% | 10% | 10% | 13% | 13% | 13% | 15%
WAGeneral ServicePilot-Ancillary HPWHProgram Dropout Rate (Attrition) | WA | General Service | Pilot-Ancillary HPWH | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Modified to reflect pilot scope |  | 1.5% | 3.5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition) |  |  | 14 Year |  | 4% | 4% | 6% | 6% | 6% | 6% | 8% | 8% | 8% | 10% | 10% | 10% | 12%
WAResidentialParent-CTA-2045 HPWHMarket Potential | WA | Residential | Parent-CTA-2045 HPWH | Market Potential | % of Eligible Customers | 2% | 5% | 9% | 13% | 18% | 23% | 29.5% | 36% | 42.5% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 50% | 10 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition) |  |  | 15 Year |  | 2% | 4% | 4% | 4% | 6% | 6% | 6% | 8% | 8% | 8% | 10% | 10% | 10% | 12%
WAResidentialParent-CTA-2045 HPWHProgram Dropout Rate (Attrition) | WA | Residential | Parent-CTA-2045 HPWH | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 50% | 10 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition) |  |  | 20 Year |  | 2% | 2% | 2% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 4% | 8% | 8% | 8% | 8% | 8% | 8% | 9%
WAGeneral ServiceParent-CTA-2045 HPWHMarket Potential | WA | General Service | Parent-CTA-2045 HPWH | Market Potential | % of Eligible Customers | 2% | 5% | 9% | 13% | 18% | 23% | 29.5% | 36% | 42.5% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 50% | 10 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServiceParent-CTA-2045 HPWHProgram Dropout Rate (Attrition) | WA | General Service | Parent-CTA-2045 HPWH | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 50% | 10 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAResidentialParent-Ancillary HPWHMarket Potential | WA | Residential | Parent-Ancillary HPWH | Market Potential | % of Eligible Customers | 2% | 5% | 9% | 13% | 18% | 23% | 29.5% | 36% | 42.5% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate (Half of eligible population) |  | 50% | 10 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAResidentialParent-Ancillary HPWHProgram Dropout Rate (Attrition) | WA | Residential | Parent-Ancillary HPWH | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate (Half of eligible population) |  | 50% | 10 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAGeneral ServiceParent-Ancillary HPWHMarket Potential | WA | General Service | Parent-Ancillary HPWH | Market Potential | % of Eligible Customers | 2% | 5% | 9% | 13% | 18% | 23% | 29.5% | 36% | 42.5% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 50% | 10 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServiceParent-Ancillary HPWHProgram Dropout Rate (Attrition) | WA | General Service | Parent-Ancillary HPWH | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 50% | 10 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAResidentialPilot-CTA-2045 ERWHMarket Potential | WA | Residential | Pilot-CTA-2045 ERWH | Market Potential | % of Eligible Customers | 4.4% | 7.04% | 8.8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 8.8% | 3.5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAResidentialPilot-CTA-2045 ERWHProgram Dropout Rate (Attrition) | WA | Residential | Pilot-CTA-2045 ERWH | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Modified to reflect pilot scope |  | 8.8% | 3.5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAGeneral ServicePilot-CTA-2045 ERWHMarket Potential | WA | General Service | Pilot-CTA-2045 ERWH | Market Potential | % of Eligible Customers | 2.5% | 4% | 5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 5% | 3.5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServicePilot-CTA-2045 ERWHProgram Dropout Rate (Attrition) | WA | General Service | Pilot-CTA-2045 ERWH | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Modified to reflect pilot scope |  | 5% | 3.5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAResidentialPilot-Ancillary ERWHMarket Potential | WA | Residential | Pilot-Ancillary ERWH | Market Potential | % of Eligible Customers | 4.4% | 7.04% | 8.8% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 8.8% | 3.5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAResidentialPilot-Ancillary ERWHProgram Dropout Rate (Attrition) | WA | Residential | Pilot-Ancillary ERWH | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Modified to reflect pilot scope |  | 8.8% | 3.5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAGeneral ServicePilot-Ancillary ERWHMarket Potential | WA | General Service | Pilot-Ancillary ERWH | Market Potential | % of Eligible Customers | 2.5% | 4% | 5% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 5% | 3.5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServicePilot-Ancillary ERWHProgram Dropout Rate (Attrition) | WA | General Service | Pilot-Ancillary ERWH | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Modified to reflect pilot scope |  | 5% | 3.5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAResidentialParent-CTA-2045 ERWHMarket Potential | WA | Residential | Parent-CTA-2045 ERWH | Market Potential | % of Eligible Customers | 7% | 9.5% | 13% | 16.5% | 21% | 25.5% | 31.5% | 37.5% | 43.5% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 50% | 11 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAResidentialParent-CTA-2045 ERWHProgram Dropout Rate (Attrition) | WA | Residential | Parent-CTA-2045 ERWH | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 50% | 11 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAGeneral ServiceParent-CTA-2045 ERWHMarket Potential | WA | General Service | Parent-CTA-2045 ERWH | Market Potential | % of Eligible Customers | 2% | 5% | 9% | 13% | 18% | 23% | 29.5% | 36% | 42.5% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 50% | 10 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServiceParent-CTA-2045 ERWHProgram Dropout Rate (Attrition) | WA | General Service | Parent-CTA-2045 ERWH | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 50% | 10 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAResidentialParent-Ancillary ERWHMarket Potential | WA | Residential | Parent-Ancillary ERWH | Market Potential | % of Eligible Customers | 7% | 9.5% | 13% | 16.5% | 21% | 25.5% | 31.5% | 37.5% | 43.5% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate (Half of eligible population) |  | 50% | 11 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAResidentialParent-Ancillary ERWHProgram Dropout Rate (Attrition) | WA | Residential | Parent-Ancillary ERWH | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate (Half of eligible population) |  | 50% | 11 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAGeneral ServiceParent-Ancillary ERWHMarket Potential | WA | General Service | Parent-Ancillary ERWH | Market Potential | % of Eligible Customers | 2% | 5% | 9% | 13% | 18% | 23% | 29.5% | 36% | 42.5% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | 50% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 50% | 10 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServiceParent-Ancillary ERWHProgram Dropout Rate (Attrition) | WA | General Service | Parent-Ancillary ERWH | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 50% | 10 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAResidentialDLC Smart AppliancesMarket Potential | WA | Residential | DLC Smart Appliances | Market Potential | % of Eligible Customers | 0.5% | 1.5% | 3.5% | 4.5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 2015 ISACA IT Risk Reward Barometer - US Consumer Results. October 2015. http://www.isaca.org/SiteCollectionDocuments/2015-risk-reward-survey/2015-isaca-risk-reward-consumer-summary-us_res_eng_1015.pdf |  | 5% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAResidentialDLC Smart AppliancesProgram Dropout Rate (Attrition) | WA | Residential | DLC Smart Appliances | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2015 ISACA IT Risk Reward Barometer - US Consumer Results. October 2015. http://www.isaca.org/SiteCollectionDocuments/2015-risk-reward-survey/2015-isaca-risk-reward-consumer-summary-us_res_eng_1015.pdf |  | 5% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAGeneral ServiceDLC Smart AppliancesMarket Potential | WA | General Service | DLC Smart Appliances | Market Potential | % of Eligible Customers | 0.5% | 1.5% | 3.5% | 4.5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 2015 ISACA IT Risk Reward Barometer - US Consumer Results. October 2015. http://www.isaca.org/SiteCollectionDocuments/2015-risk-reward-survey/2015-isaca-risk-reward-consumer-summary-us_res_eng_1015.pdf |  | 5% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServiceDLC Smart AppliancesProgram Dropout Rate (Attrition) | WA | General Service | DLC Smart Appliances | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2015 ISACA IT Risk Reward Barometer - US Consumer Results. October 2015. http://www.isaca.org/SiteCollectionDocuments/2015-risk-reward-survey/2015-isaca-risk-reward-consumer-summary-us_res_eng_1015.pdf |  | 5% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WARes-EVDLC Electric Vehicle ChargingMarket Potential | WA | Res-EV | DLC Electric Vehicle Charging | Market Potential | % of Eligible Customers | 2% | 6% | 14% | 18% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | WA: 2024 Avista Update; Lowered from 1/3 of EV TOU rate (17%) to 15% based on Avista feedback |  | 20% | 5 | 1% | Res-EVSteady State Participation Rate | Res-EVProgram ramp up period | Market PotentialWA | Res-EVProgram Dropout Rate (Attrition)
WARes-EVDLC Electric Vehicle ChargingProgram Dropout Rate (Attrition) | WA | Res-EV | DLC Electric Vehicle Charging | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | WA: 2024 Avista Update; Lowered from 1/3 of EV TOU rate (17%) to 15% based on Avista feedback |  | 20% | 5 | 1% | Res-EVSteady State Participation Rate | Res-EVProgram ramp up period | Market PotentialWA | Res-EVProgram Dropout Rate (Attrition)
WAGS-EVDLC Electric Vehicle ChargingMarket Potential | WA | GS-EV | DLC Electric Vehicle Charging | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | GS-EVSteady State Participation Rate | GS-EVProgram ramp up period | Market PotentialWA | GS-EVProgram Dropout Rate (Attrition)
WAGS-EVDLC Electric Vehicle ChargingProgram Dropout Rate (Attrition) | WA | GS-EV | DLC Electric Vehicle Charging | Program Dropout Rate (Attrition) | % | [30 empty] | GS-EVSteady State Participation Rate | GS-EVProgram ramp up period | Market PotentialWA | GS-EVProgram Dropout Rate (Attrition)
WARes-EVAncillary EVMarket Potential | WA | Res-EV | Ancillary EV | Market Potential | % of Eligible Customers | 1.5% | 4.5% | 10.5% | 13.5% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | Assumption: One Third of TOU Demand Rate w EV. This participation rate will be throttled / scaled using the equipment saturation for EVs, which will be quite low. |  | 15% | 5 | 1% | Res-EVSteady State Participation Rate | Res-EVProgram ramp up period | Market PotentialWA | Res-EVProgram Dropout Rate (Attrition)
WARes-EVAncillary EVProgram Dropout Rate (Attrition) | WA | Res-EV | Ancillary EV | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Assumption: One Third of TOU Demand Rate w EV. This participation rate will be throttled / scaled using the equipment saturation for EVs, which will be quite low. |  | 15% | 5 | 1% | Res-EVSteady State Participation Rate | Res-EVProgram ramp up period | Market PotentialWA | Res-EVProgram Dropout Rate (Attrition)
WAGS-EVAncillary EVMarket Potential | WA | GS-EV | Ancillary EV | Market Potential | % of Eligible Customers | 1.5% | 4.5% | 10.5% | 13.5% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | Prelim Assumption: One Third of EV TOU Demand Rate |  | 15% | 5 | 1% | GS-EVSteady State Participation Rate | GS-EVProgram ramp up period | Market PotentialWA | GS-EVProgram Dropout Rate (Attrition)
WAGS-EVAncillary EVProgram Dropout Rate (Attrition) | WA | GS-EV | Ancillary EV | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Prelim Assumption: One Third of EV TOU Demand Rate |  | 15% | 5 | 1% | GS-EVSteady State Participation Rate | GS-EVProgram ramp up period | Market PotentialWA | GS-EVProgram Dropout Rate (Attrition)
WAGeneral ServiceThird Party ContractsMarket Potential | WA | General Service | Third Party Contracts | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServiceThird Party ContractsProgram Dropout Rate (Attrition) | WA | General Service | Third Party Contracts | Program Dropout Rate (Attrition) | % | [30 empty] | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WALarge General ServiceThird Party ContractsMarket Potential | WA | Large General Service | Third Party Contracts | Market Potential | % of Eligible Customers | 7.5% | 12% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 2024 Avista Update |  | 15% | 3 | 1% | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialWA | Large General ServiceProgram Dropout Rate (Attrition)
WALarge General ServiceThird Party ContractsProgram Dropout Rate (Attrition) | WA | Large General Service | Third Party Contracts | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2024 Avista Update |  | 15% | 3 | 1% | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialWA | Large General ServiceProgram Dropout Rate (Attrition)
WAExtra Large General ServiceThird Party ContractsMarket Potential | WA | Extra Large General Service | Third Party Contracts | Market Potential | % of Eligible Customers | 7.5% | 12% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 2024 Avista Update |  | 15% | 3 | 1% | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialWA | Extra Large General ServiceProgram Dropout Rate (Attrition)
WAExtra Large General ServiceThird Party ContractsProgram Dropout Rate (Attrition) | WA | Extra Large General Service | Third Party Contracts | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2024 Avista Update |  | 15% | 3 | 1% | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialWA | Extra Large General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServiceAncillary Third PartyMarket Potential | WA | General Service | Ancillary Third Party | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServiceAncillary Third PartyProgram Dropout Rate (Attrition) | WA | General Service | Ancillary Third Party | Program Dropout Rate (Attrition) | % | [30 empty] | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WALarge General ServiceAncillary Third PartyMarket Potential | WA | Large General Service | Ancillary Third Party | Market Potential | % of Eligible Customers | 1.369% | 2.19% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | Participation rate based on 2020 EE Study saturations of EMS systems within Avista commercial customers, weighted by segment size. |  | 2.737% | 3 | 1% | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialWA | Large General ServiceProgram Dropout Rate (Attrition)
WALarge General ServiceAncillary Third PartyProgram Dropout Rate (Attrition) | WA | Large General Service | Ancillary Third Party | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Participation rate based on 2020 EE Study saturations of EMS systems within Avista commercial customers, weighted by segment size. |  | 2.737% | 3 | 1% | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialWA | Large General ServiceProgram Dropout Rate (Attrition)
WAExtra Large General ServiceAncillary Third PartyMarket Potential | WA | Extra Large General Service | Ancillary Third Party | Market Potential | % of Eligible Customers | 1.369% | 2.19% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | 2.737% | Participation rate based on 2020 EE Study saturations of EMS systems within Avista commercial customers, weighted by segment size. |  | 2.737% | 3 | 1% | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialWA | Extra Large General ServiceProgram Dropout Rate (Attrition)
WAExtra Large General ServiceAncillary Third PartyProgram Dropout Rate (Attrition) | WA | Extra Large General Service | Ancillary Third Party | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Participation rate based on 2020 EE Study saturations of EMS systems within Avista commercial customers, weighted by segment size. |  | 2.737% | 3 | 1% | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialWA | Extra Large General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServiceThermal Energy StorageMarket Potential | WA | General Service | Thermal Energy Storage | Market Potential | % of Eligible Customers | 0.05% | 0.15% | 0.35% | 0.45% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | Don't expect much participation - 0.5% |  | 0.5% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServiceThermal Energy StorageProgram Dropout Rate (Attrition) | WA | General Service | Thermal Energy Storage | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Don't expect much participation - 0.5% |  | 0.5% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WALarge General ServiceThermal Energy StorageMarket Potential | WA | Large General Service | Thermal Energy Storage | Market Potential | % of Eligible Customers | 0.15% | 0.45% | 1.05% | 1.35% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | Low participation is 1/2 DLC CAC |  | 1.5% | 5 | 1% | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialWA | Large General ServiceProgram Dropout Rate (Attrition)
WALarge General ServiceThermal Energy StorageProgram Dropout Rate (Attrition) | WA | Large General Service | Thermal Energy Storage | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Low participation is 1/2 DLC CAC |  | 1.5% | 5 | 1% | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialWA | Large General ServiceProgram Dropout Rate (Attrition)
WAExtra Large General ServiceThermal Energy StorageMarket Potential | WA | Extra Large General Service | Thermal Energy Storage | Market Potential | % of Eligible Customers | 0.15% | 0.45% | 1.05% | 1.35% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | Low participation is 1/2 DLC CAC |  | 1.5% | 5 | 1% | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialWA | Extra Large General ServiceProgram Dropout Rate (Attrition)
WAExtra Large General ServiceThermal Energy StorageProgram Dropout Rate (Attrition) | WA | Extra Large General Service | Thermal Energy Storage | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Low participation is 1/2 DLC CAC |  | 1.5% | 5 | 1% | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialWA | Extra Large General ServiceProgram Dropout Rate (Attrition)
WAResidentialBattery Energy StorageMarket Potential | WA | Residential | Battery Energy Storage | Market Potential | % of Eligible Customers | 0.7436% | 2.231% | 5.206% | 6.693% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | PAC saw ~2.23% of solar PV customers participate in a battery DR program in year 2 of the program. (https://www.pacificorp.com/content/dam/pcorp/documents/en/pacificorp/environment/dsm/utah/2022_Utah_Wattsmart_Business_Energy_Eff_Peak_Reduction.pdf), solar PV # from DNV PG Study |  | 7.436% | 5 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAResidentialBattery Energy StorageProgram Dropout Rate (Attrition) | WA | Residential | Battery Energy Storage | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | PAC saw ~2.23% of solar PV customers participate in a battery DR program in year 2 of the program. (https://www.pacificorp.com/content/dam/pcorp/documents/en/pacificorp/environment/dsm/utah/2022_Utah_Wattsmart_Business_Energy_Eff_Peak_Reduction.pdf), solar PV # from DNV PG Study |  | 7.436% | 5 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAGeneral ServiceBattery Energy StorageMarket Potential | WA | General Service | Battery Energy Storage | Market Potential | % of Eligible Customers | 0.1487% | 0.2975% | 0.5949% | 0.8924% | 1.19% | 1.636% | 2.082% | 2.528% | 3.123% | 3.718% | 4.313% | 5.057% | 5.8% | 6.544% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | Same as Residential |  | 7.436% | 15 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServiceBattery Energy StorageProgram Dropout Rate (Attrition) | WA | General Service | Battery Energy Storage | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Same as Residential |  | 7.436% | 15 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WALarge General ServiceBattery Energy StorageMarket Potential | WA | Large General Service | Battery Energy Storage | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialWA | Large General ServiceProgram Dropout Rate (Attrition)
WALarge General ServiceBattery Energy StorageProgram Dropout Rate (Attrition) | WA | Large General Service | Battery Energy Storage | Program Dropout Rate (Attrition) | % | [30 empty] | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialWA | Large General ServiceProgram Dropout Rate (Attrition)
WAExtra Large General ServiceBattery Energy StorageMarket Potential | WA | Extra Large General Service | Battery Energy Storage | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialWA | Extra Large General ServiceProgram Dropout Rate (Attrition)
WAExtra Large General ServiceBattery Energy StorageProgram Dropout Rate (Attrition) | WA | Extra Large General Service | Battery Energy Storage | Program Dropout Rate (Attrition) | % | [30 empty] | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialWA | Extra Large General ServiceProgram Dropout Rate (Attrition)
WAResidentialAncillary Battery StorageMarket Potential | WA | Residential | Ancillary Battery Storage | Market Potential | % of Eligible Customers | 0.01% | 0.02% | 0.04% | 0.06% | 0.08% | 0.11% | 0.14% | 0.17% | 0.21% | 0.25% | 0.29% | 0.34% | 0.39% | 0.44% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 20% from MISO LRZ 7. Assuming half for high and half again for low. *halved again 9-14-17, as per discussion with Kelly - potential looked too high. Pacificorp study didn't consider this program |  | 0.5% | 15 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAResidentialAncillary Battery StorageProgram Dropout Rate (Attrition) | WA | Residential | Ancillary Battery Storage | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 20% from MISO LRZ 7. Assuming half for high and half again for low. *halved again 9-14-17, as per discussion with Kelly - potential looked too high. Pacificorp study didn't consider this program |  | 0.5% | 15 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAGeneral ServiceAncillary Battery StorageMarket Potential | WA | General Service | Ancillary Battery Storage | Market Potential | % of Eligible Customers | 0.01% | 0.02% | 0.04% | 0.06% | 0.08% | 0.11% | 0.14% | 0.17% | 0.21% | 0.25% | 0.29% | 0.34% | 0.39% | 0.44% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | Same as Residential |  | 0.5% | 15 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServiceAncillary Battery StorageProgram Dropout Rate (Attrition) | WA | General Service | Ancillary Battery Storage | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Same as Residential |  | 0.5% | 15 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WALarge General ServiceAncillary Battery StorageMarket Potential | WA | Large General Service | Ancillary Battery Storage | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialWA | Large General ServiceProgram Dropout Rate (Attrition)
WALarge General ServiceAncillary Battery StorageProgram Dropout Rate (Attrition) | WA | Large General Service | Ancillary Battery Storage | Program Dropout Rate (Attrition) | % | [30 empty] | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialWA | Large General ServiceProgram Dropout Rate (Attrition)
WAExtra Large General ServiceAncillary Battery StorageMarket Potential | WA | Extra Large General Service | Ancillary Battery Storage | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialWA | Extra Large General ServiceProgram Dropout Rate (Attrition)
WAExtra Large General ServiceAncillary Battery StorageProgram Dropout Rate (Attrition) | WA | Extra Large General Service | Ancillary Battery Storage | Program Dropout Rate (Attrition) | % | [30 empty] | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialWA | Extra Large General ServiceProgram Dropout Rate (Attrition)
WAResidentialBehavioralMarket Potential | WA | Residential | Behavioral | Market Potential | % of Eligible Customers | 10% | 16% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | high rate based on PG&E rollout with six waves http://www.calmac.org/publications/DNVGL_PGE_HERs_2015_final_to_calmac.pdf --> PC study has high case at 20% |  | 20% | 3 | 2% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAResidentialBehavioralProgram Dropout Rate (Attrition) | WA | Residential | Behavioral | Program Dropout Rate (Attrition) | % | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | high rate based on PG&E rollout with six waves http://www.calmac.org/publications/DNVGL_PGE_HERs_2015_final_to_calmac.pdf --> PC study has high case at 20% |  | 20% | 3 | 2% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAResidentialPilot-Time-of-Use Opt-inMarket Potential | WA | Residential | Pilot-Time-of-Use Opt-in | Market Potential | % of Eligible Customers | 0.205% | 0.328% | 0.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified for pilot scope |  | 0.41% | 3.5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAResidentialPilot-Time-of-Use Opt-inProgram Dropout Rate (Attrition) | WA | Residential | Pilot-Time-of-Use Opt-in | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Modified for pilot scope |  | 0.41% | 3.5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAGeneral ServicePilot-Time-of-Use Opt-inMarket Potential | WA | General Service | Pilot-Time-of-Use Opt-in | Market Potential | % of Eligible Customers | 0.205% | 0.328% | 0.41% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified for pilot scope |  | 0.41% | 3.5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServicePilot-Time-of-Use Opt-inProgram Dropout Rate (Attrition) | WA | General Service | Pilot-Time-of-Use Opt-in | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Modified for pilot scope |  | 0.41% | 3.5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAResidentialParent-Time-of-Use Opt-inMarket Potential | WA | Residential | Parent-Time-of-Use Opt-in | Market Potential | % of Eligible Customers | 0.8198% | 0.8086% | 2% | 3.9% | 9.1% | 11.7% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | Brattle Analysis and Estimate |  | 13% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAResidentialParent-Time-of-Use Opt-inProgram Dropout Rate (Attrition) | WA | Residential | Parent-Time-of-Use Opt-in | Program Dropout Rate (Attrition) | % | 0% | 0% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Brattle Analysis and Estimate |  | 13% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAGeneral ServiceParent-Time-of-Use Opt-inMarket Potential | WA | General Service | Parent-Time-of-Use Opt-in | Market Potential | % of Eligible Customers | 4.115% | 4.074% | 5% | 5.5% | 6% | 6.5% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 2024 Avista Update |  | 7% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServiceParent-Time-of-Use Opt-inProgram Dropout Rate (Attrition) | WA | General Service | Parent-Time-of-Use Opt-in | Program Dropout Rate (Attrition) | % | 0% | 0% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2024 Avista Update |  | 7% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WALarge General ServiceParent-Time-of-Use Opt-inMarket Potential | WA | Large General Service | Parent-Time-of-Use Opt-in | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialWA | Large General ServiceProgram Dropout Rate (Attrition)
WALarge General ServiceParent-Time-of-Use Opt-inProgram Dropout Rate (Attrition) | WA | Large General Service | Parent-Time-of-Use Opt-in | Program Dropout Rate (Attrition) | % | [30 empty] | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialWA | Large General ServiceProgram Dropout Rate (Attrition)
WAExtra Large General ServiceParent-Time-of-Use Opt-inMarket Potential | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialWA | Extra Large General ServiceProgram Dropout Rate (Attrition)
WAExtra Large General ServiceParent-Time-of-Use Opt-inProgram Dropout Rate (Attrition) | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Program Dropout Rate (Attrition) | % | [30 empty] | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialWA | Extra Large General ServiceProgram Dropout Rate (Attrition)
WAResidentialTime-of-Use Opt-OutMarket Potential | WA | Residential | Time-of-Use Opt-Out | Market Potential | % of Eligible Customers | 100% | 85.4% | 78.9% | 75.6% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 2024 Avista Update |  | 20% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAResidentialTime-of-Use Opt-OutProgram Dropout Rate (Attrition) | WA | Residential | Time-of-Use Opt-Out | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2024 Avista Update |  | 20% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAGeneral ServiceTime-of-Use Opt-OutMarket Potential | WA | General Service | Time-of-Use Opt-Out | Market Potential | % of Eligible Customers | 100% | 85.4% | 78.9% | 75.6% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 2024 Avista Update |  | 20% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServiceTime-of-Use Opt-OutProgram Dropout Rate (Attrition) | WA | General Service | Time-of-Use Opt-Out | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2024 Avista Update |  | 20% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WALarge General ServiceTime-of-Use Opt-OutMarket Potential | WA | Large General Service | Time-of-Use Opt-Out | Market Potential | % of Eligible Customers | 100% | 85.4% | 78.9% | 75.6% | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialWA | Large General ServiceProgram Dropout Rate (Attrition)
WALarge General ServiceTime-of-Use Opt-OutProgram Dropout Rate (Attrition) | WA | Large General Service | Time-of-Use Opt-Out | Program Dropout Rate (Attrition) | % | [30 empty] | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialWA | Large General ServiceProgram Dropout Rate (Attrition)
WAExtra Large General ServiceTime-of-Use Opt-OutMarket Potential | WA | Extra Large General Service | Time-of-Use Opt-Out | Market Potential | % of Eligible Customers | 100% | 85.4% | 78.9% | 75.6% | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialWA | Extra Large General ServiceProgram Dropout Rate (Attrition)
WAExtra Large General ServiceTime-of-Use Opt-OutProgram Dropout Rate (Attrition) | WA | Extra Large General Service | Time-of-Use Opt-Out | Program Dropout Rate (Attrition) | % | [30 empty] | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialWA | Extra Large General ServiceProgram Dropout Rate (Attrition)
WAGS-EVElectric Vehicle TOU Opt-inMarket Potential | WA | GS-EV | Electric Vehicle TOU Opt-in | Market Potential | % of Eligible Customers | 2% | 6% | 14% | 18% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 2024 Avista Update: sch 13 |  | 20% | 5 | 1% | GS-EVSteady State Participation Rate | GS-EVProgram ramp up period | Market PotentialWA | GS-EVProgram Dropout Rate (Attrition)
WAGS-EVElectric Vehicle TOU Opt-inProgram Dropout Rate (Attrition) | WA | GS-EV | Electric Vehicle TOU Opt-in | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2024 Avista Update: sch 13 |  | 20% | 5 | 1% | GS-EVSteady State Participation Rate | GS-EVProgram ramp up period | Market PotentialWA | GS-EVProgram Dropout Rate (Attrition)
WALGS-EVElectric Vehicle TOU Opt-inMarket Potential | WA | LGS-EV | Electric Vehicle TOU Opt-in | Market Potential | % of Eligible Customers | 1% | 3% | 7% | 9% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 2024 Avista Update: sch 23 |  | 10% | 5 | 1% | LGS-EVSteady State Participation Rate | LGS-EVProgram ramp up period | Market PotentialWA | LGS-EVProgram Dropout Rate (Attrition)
WALGS-EVElectric Vehicle TOU Opt-inProgram Dropout Rate (Attrition) | WA | LGS-EV | Electric Vehicle TOU Opt-in | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2024 Avista Update: sch 23 |  | 10% | 5 | 1% | LGS-EVSteady State Participation Rate | LGS-EVProgram ramp up period | Market PotentialWA | LGS-EVProgram Dropout Rate (Attrition)
WAResidentialParent-Peak Time RebateMarket Potential | WA | Residential | Parent-Peak Time Rebate | Market Potential | % of Eligible Customers | 0.4099% | 0.4043% | 1.5% | 4.5% | 10.5% | 13.5% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: Goal of 110,000 out of ~800,000 residential customers (see table below) |  | 15% | 5 | 2% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAResidentialParent-Peak Time RebateProgram Dropout Rate (Attrition) | WA | Residential | Parent-Peak Time Rebate | Program Dropout Rate (Attrition) | % | 0% | 0% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: Goal of 110,000 out of ~800,000 residential customers (see table below) |  | 15% | 5 | 2% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAGeneral ServiceParent-Peak Time RebateMarket Potential | WA | General Service | Parent-Peak Time Rebate | Market Potential | % of Eligible Customers | 2.057% | 2.037% | 1.5% | 4.5% | 10.5% | 13.5% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: Goal of 110,000 out of ~800,000 residential customers (see table below) |  | 15% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServiceParent-Peak Time RebateProgram Dropout Rate (Attrition) | WA | General Service | Parent-Peak Time Rebate | Program Dropout Rate (Attrition) | % | 0% | 0% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: Goal of 110,000 out of ~800,000 residential customers (see table below) |  | 15% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAResidentialPilot-Peak Time RebateMarket Potential | WA | Residential | Pilot-Peak Time Rebate | Market Potential | % of Eligible Customers | 0.095% | 0.152% | 0.19% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified for pilot scope |  | 0.19% | 3.5 | 2% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAResidentialPilot-Peak Time RebateProgram Dropout Rate (Attrition) | WA | Residential | Pilot-Peak Time Rebate | Program Dropout Rate (Attrition) | % | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | Modified for pilot scope |  | 0.19% | 3.5 | 2% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialWA | ResidentialProgram Dropout Rate (Attrition)
WAGeneral ServicePilot-Peak Time RebateMarket Potential | WA | General Service | Pilot-Peak Time Rebate | Market Potential | % of Eligible Customers | 0.095% | 0.152% | 0.19% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified for pilot scope |  | 0.19% | 3.5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WAGeneral ServicePilot-Peak Time RebateProgram Dropout Rate (Attrition) | WA | General Service | Pilot-Peak Time Rebate | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Modified for pilot scope |  | 0.19% | 3.5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialWA | General ServiceProgram Dropout Rate (Attrition)
WALarge General ServiceVariable Peak Pricing RatesMarket Potential | WA | Large General Service | Variable Peak Pricing Rates | Market Potential | % of Eligible Customers | 2.5% | 7.5% | 17.5% | 22.5% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | High Case- OG&E's VPP Plus participation rate- should be 103000/400000 around 25% |  | 25% | 5 | 1% | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialWA | Large General ServiceProgram Dropout Rate (Attrition)
WALarge General ServiceVariable Peak Pricing RatesProgram Dropout Rate (Attrition) | WA | Large General Service | Variable Peak Pricing Rates | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | High Case- OG&E's VPP Plus participation rate- should be 103000/400000 around 25% |  | 25% | 5 | 1% | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialWA | Large General ServiceProgram Dropout Rate (Attrition)
WAExtra Large General ServiceVariable Peak Pricing RatesMarket Potential | WA | Extra Large General Service | Variable Peak Pricing Rates | Market Potential | % of Eligible Customers | 2.5% | 7.5% | 17.5% | 22.5% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | High Case- OG&E's VPP Plus participation rate |  | 25% | 5 | 2% | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialWA | Extra Large General ServiceProgram Dropout Rate (Attrition)
WAExtra Large General ServiceVariable Peak Pricing RatesProgram Dropout Rate (Attrition) | WA | Extra Large General Service | Variable Peak Pricing Rates | Program Dropout Rate (Attrition) | % | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | High Case- OG&E's VPP Plus participation rate |  | 25% | 5 | 2% | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialWA | Extra Large General ServiceProgram Dropout Rate (Attrition)
IDResidentialDLC Central ACMarket Potential | ID | Residential | DLC Central AC | Market Potential | % of Eligible Customers | 1% | 3% | 7% | 9% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | NWPC DLC Switch cooling assumption- 5 yr ramp rate |  | 10% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialDLC Central ACProgram Dropout Rate (Attrition) | ID | Residential | DLC Central AC | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | NWPC DLC Switch cooling assumption- 5 yr ramp rate |  | 10% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServiceDLC Central ACMarket Potential | ID | General Service | DLC Central AC | Market Potential | % of Eligible Customers | 1% | 3% | 7% | 9% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | NWPC DLC Switch cooling assumption- 5 yr ramp rate |  | 10% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceDLC Central ACProgram Dropout Rate (Attrition) | ID | General Service | DLC Central AC | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | NWPC DLC Switch cooling assumption- 5 yr ramp rate |  | 10% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDResidentialDLC Smart Thermostats - CoolingMarket Potential | ID | Residential | DLC Smart Thermostats - Cooling | Market Potential | % of Eligible Customers | 2% | 6% | 14% | 18% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | NWPC Smart Thermostat cooling assumption- 5 yr ramp rate |  | 20% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialDLC Smart Thermostats - CoolingProgram Dropout Rate (Attrition) | ID | Residential | DLC Smart Thermostats - Cooling | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | NWPC Smart Thermostat cooling assumption- 5 yr ramp rate |  | 20% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServiceDLC Smart Thermostats - CoolingMarket Potential | ID | General Service | DLC Smart Thermostats - Cooling | Market Potential | % of Eligible Customers | 1% | 3% | 7% | 9% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 2024 Avista Update |  | 10% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceDLC Smart Thermostats - CoolingProgram Dropout Rate (Attrition) | ID | General Service | DLC Smart Thermostats - Cooling | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2024 Avista Update |  | 10% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDResidentialAncillary CoolingMarket Potential | ID | Residential | Ancillary Cooling | Market Potential | % of Eligible Customers | 1% | 3% | 7% | 9% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | Half of Thermostat Participation given an additional $20 as incentive |  | 10% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialAncillary CoolingProgram Dropout Rate (Attrition) | ID | Residential | Ancillary Cooling | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Half of Thermostat Participation given an additional $20 as incentive |  | 10% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServiceAncillary CoolingMarket Potential | ID | General Service | Ancillary Cooling | Market Potential | % of Eligible Customers | 1% | 3% | 7% | 9% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | NWPC Smart Thermostat cooling assumption- 5 yr ramp rate- Half for Ancillary |  | 10% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceAncillary CoolingProgram Dropout Rate (Attrition) | ID | General Service | Ancillary Cooling | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | NWPC Smart Thermostat cooling assumption- 5 yr ramp rate- Half for Ancillary |  | 10% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDResidentialDLC Smart Thermostats - HeatingMarket Potential | ID | Residential | DLC Smart Thermostats - Heating | Market Potential | % of Eligible Customers | 0.5% | 1.5% | 3.5% | 4.5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | Assuming maximum participation for combined DLC Cooling and Smart Therm is 25%, reduced from 30% to account for those program participants who may have intended to participate but were unable to correctly install their thermostat |  | 5% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialDLC Smart Thermostats - HeatingProgram Dropout Rate (Attrition) | ID | Residential | DLC Smart Thermostats - Heating | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Assuming maximum participation for combined DLC Cooling and Smart Therm is 25%, reduced from 30% to account for those program participants who may have intended to participate but were unable to correctly install their thermostat |  | 5% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServiceDLC Smart Thermostats - HeatingMarket Potential | ID | General Service | DLC Smart Thermostats - Heating | Market Potential | % of Eligible Customers | 0.3% | 0.9% | 2.1% | 2.7% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | Dropping to 3% to compensate for higher space heating saturations |  | 3% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceDLC Smart Thermostats - HeatingProgram Dropout Rate (Attrition) | ID | General Service | DLC Smart Thermostats - Heating | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Dropping to 3% to compensate for higher space heating saturations |  | 3% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDResidentialDLC Water HeatingMarket Potential | ID | Residential | DLC Water Heating | Market Potential | % of Eligible Customers | 1.5% | 4.5% | 10.5% | 13.5% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | Ensure population applies to the subset of customers participating in AC or Space Heating DLC- 25% max using studies from PLMA, BGE, and Brattle |  | 15% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialDLC Water HeatingProgram Dropout Rate (Attrition) | ID | Residential | DLC Water Heating | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Ensure population applies to the subset of customers participating in AC or Space Heating DLC- 25% max using studies from PLMA, BGE, and Brattle |  | 15% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServiceDLC Water HeatingMarket Potential | ID | General Service | DLC Water Heating | Market Potential | % of Eligible Customers | 0.5% | 1.5% | 3.5% | 4.5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | * Changed from 3% to reflect a Brattle Study to the left that estimates 5-10% |  | 5% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceDLC Water HeatingProgram Dropout Rate (Attrition) | ID | General Service | DLC Water Heating | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | * Changed from 3% to reflect a Brattle Study to the left that estimates 5-10% |  | 5% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDResidentialAncillary DLC WHMarket Potential | ID | Residential | Ancillary DLC WH | Market Potential | % of Eligible Customers | 1.5% | 4.5% | 10.5% | 13.5% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | Ensure population applies to the subset of customers participating in AC or Space Heating DLC |  | 15% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialAncillary DLC WHProgram Dropout Rate (Attrition) | ID | Residential | Ancillary DLC WH | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Ensure population applies to the subset of customers participating in AC or Space Heating DLC |  | 15% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServiceAncillary DLC WHMarket Potential | ID | General Service | Ancillary DLC WH | Market Potential | % of Eligible Customers | 0.5% | 1.5% | 3.5% | 4.5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | * Changed from 3% to reflect a Brattle Study to the left that estimates 5-10% |  | 5% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceAncillary DLC WHProgram Dropout Rate (Attrition) | ID | General Service | Ancillary DLC WH | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | * Changed from 3% to reflect a Brattle Study to the left that estimates 5-10% |  | 5% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDResidentialAncillary HeatingMarket Potential | ID | Residential | Ancillary Heating | Market Potential | % of Eligible Customers | 0.25% | 0.75% | 1.75% | 2.25% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | Half for ancillary |  | 2.5% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialAncillary HeatingProgram Dropout Rate (Attrition) | ID | Residential | Ancillary Heating | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Half for ancillary |  | 2.5% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServiceAncillary HeatingMarket Potential | ID | General Service | Ancillary Heating | Market Potential | % of Eligible Customers | 0.15% | 0.45% | 1.05% | 1.35% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | Dropping to 3% to compensate for higher space heating saturations- half for ancillary |  | 1.5% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceAncillary HeatingProgram Dropout Rate (Attrition) | ID | General Service | Ancillary Heating | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Dropping to 3% to compensate for higher space heating saturations- half for ancillary |  | 1.5% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDResidentialPilot-CTA-2045 HPWHMarket Potential | ID | Residential | Pilot-CTA-2045 HPWH | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialPilot-CTA-2045 HPWHProgram Dropout Rate (Attrition) | ID | Residential | Pilot-CTA-2045 HPWH | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServicePilot-CTA-2045 HPWHMarket Potential | ID | General Service | Pilot-CTA-2045 HPWH | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServicePilot-CTA-2045 HPWHProgram Dropout Rate (Attrition) | ID | General Service | Pilot-CTA-2045 HPWH | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDResidentialPilot-Ancillary HPWHMarket Potential | ID | Residential | Pilot-Ancillary HPWH | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialPilot-Ancillary HPWHProgram Dropout Rate (Attrition) | ID | Residential | Pilot-Ancillary HPWH | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServicePilot-Ancillary HPWHMarket Potential | ID | General Service | Pilot-Ancillary HPWH | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServicePilot-Ancillary HPWHProgram Dropout Rate (Attrition) | ID | General Service | Pilot-Ancillary HPWH | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDResidentialParent-CTA-2045 HPWHMarket Potential | ID | Residential | Parent-CTA-2045 HPWH | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialParent-CTA-2045 HPWHProgram Dropout Rate (Attrition) | ID | Residential | Parent-CTA-2045 HPWH | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServiceParent-CTA-2045 HPWHMarket Potential | ID | General Service | Parent-CTA-2045 HPWH | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceParent-CTA-2045 HPWHProgram Dropout Rate (Attrition) | ID | General Service | Parent-CTA-2045 HPWH | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDResidentialParent-Ancillary HPWHMarket Potential | ID | Residential | Parent-Ancillary HPWH | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate (Half of eligible population) |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialParent-Ancillary HPWHProgram Dropout Rate (Attrition) | ID | Residential | Parent-Ancillary HPWH | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate (Half of eligible population) |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServiceParent-Ancillary HPWHMarket Potential | ID | General Service | Parent-Ancillary HPWH | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceParent-Ancillary HPWHProgram Dropout Rate (Attrition) | ID | General Service | Parent-Ancillary HPWH | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDResidentialPilot-CTA-2045 ERWHMarket Potential | ID | Residential | Pilot-CTA-2045 ERWH | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialPilot-CTA-2045 ERWHProgram Dropout Rate (Attrition) | ID | Residential | Pilot-CTA-2045 ERWH | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServicePilot-CTA-2045 ERWHMarket Potential | ID | General Service | Pilot-CTA-2045 ERWH | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServicePilot-CTA-2045 ERWHProgram Dropout Rate (Attrition) | ID | General Service | Pilot-CTA-2045 ERWH | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDResidentialPilot-Ancillary ERWHMarket Potential | ID | Residential | Pilot-Ancillary ERWH | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialPilot-Ancillary ERWHProgram Dropout Rate (Attrition) | ID | Residential | Pilot-Ancillary ERWH | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServicePilot-Ancillary ERWHMarket Potential | ID | General Service | Pilot-Ancillary ERWH | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServicePilot-Ancillary ERWHProgram Dropout Rate (Attrition) | ID | General Service | Pilot-Ancillary ERWH | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified to reflect pilot scope |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDResidentialParent-CTA-2045 ERWHMarket Potential | ID | Residential | Parent-CTA-2045 ERWH | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialParent-CTA-2045 ERWHProgram Dropout Rate (Attrition) | ID | Residential | Parent-CTA-2045 ERWH | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServiceParent-CTA-2045 ERWHMarket Potential | ID | General Service | Parent-CTA-2045 ERWH | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceParent-CTA-2045 ERWHProgram Dropout Rate (Attrition) | ID | General Service | Parent-CTA-2045 ERWH | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDResidentialParent-Ancillary ERWHMarket Potential | ID | Residential | Parent-Ancillary ERWH | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate (Half of eligible population) |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialParent-Ancillary ERWHProgram Dropout Rate (Attrition) | ID | Residential | Parent-Ancillary ERWH | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate (Half of eligible population) |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServiceParent-Ancillary ERWHMarket Potential | ID | General Service | Parent-Ancillary ERWH | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceParent-Ancillary ERWHProgram Dropout Rate (Attrition) | ID | General Service | Parent-Ancillary ERWH | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDResidentialDLC Smart AppliancesMarket Potential | ID | Residential | DLC Smart Appliances | Market Potential | % of Eligible Customers | 0.5% | 1.5% | 3.5% | 4.5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 2015 ISACA IT Risk Reward Barometer - US Consumer Results. October 2015. http://www.isaca.org/SiteCollectionDocuments/2015-risk-reward-survey/2015-isaca-risk-reward-consumer-summary-us_res_eng_1015.pdf |  | 5% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialDLC Smart AppliancesProgram Dropout Rate (Attrition) | ID | Residential | DLC Smart Appliances | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2015 ISACA IT Risk Reward Barometer - US Consumer Results. October 2015. http://www.isaca.org/SiteCollectionDocuments/2015-risk-reward-survey/2015-isaca-risk-reward-consumer-summary-us_res_eng_1015.pdf |  | 5% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServiceDLC Smart AppliancesMarket Potential | ID | General Service | DLC Smart Appliances | Market Potential | % of Eligible Customers | 0.5% | 1.5% | 3.5% | 4.5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 5% | 2015 ISACA IT Risk Reward Barometer - US Consumer Results. October 2015. http://www.isaca.org/SiteCollectionDocuments/2015-risk-reward-survey/2015-isaca-risk-reward-consumer-summary-us_res_eng_1015.pdf |  | 5% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceDLC Smart AppliancesProgram Dropout Rate (Attrition) | ID | General Service | DLC Smart Appliances | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2015 ISACA IT Risk Reward Barometer - US Consumer Results. October 2015. http://www.isaca.org/SiteCollectionDocuments/2015-risk-reward-survey/2015-isaca-risk-reward-consumer-summary-us_res_eng_1015.pdf |  | 5% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDRes-EVDLC Electric Vehicle ChargingMarket Potential | ID | Res-EV | DLC Electric Vehicle Charging | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | WA: 2024 Avista Update; Lowered from 1/3 of EV TOU rate (17%) to 15% based on Avista feedback |  | 0% | 0 | 0% | Res-EVSteady State Participation Rate | Res-EVProgram ramp up period | Market PotentialID | Res-EVProgram Dropout Rate (Attrition)
IDRes-EVDLC Electric Vehicle ChargingProgram Dropout Rate (Attrition) | ID | Res-EV | DLC Electric Vehicle Charging | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | WA: 2024 Avista Update; Lowered from 1/3 of EV TOU rate (17%) to 15% based on Avista feedback |  | 0% | 0 | 0% | Res-EVSteady State Participation Rate | Res-EVProgram ramp up period | Market PotentialID | Res-EVProgram Dropout Rate (Attrition)
IDGS-EVDLC Electric Vehicle ChargingMarket Potential | ID | GS-EV | DLC Electric Vehicle Charging | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | GS-EVSteady State Participation Rate | GS-EVProgram ramp up period | Market PotentialID | GS-EVProgram Dropout Rate (Attrition)
IDGS-EVDLC Electric Vehicle ChargingProgram Dropout Rate (Attrition) | ID | GS-EV | DLC Electric Vehicle Charging | Program Dropout Rate (Attrition) | % | [30 empty] | GS-EVSteady State Participation Rate | GS-EVProgram ramp up period | Market PotentialID | GS-EVProgram Dropout Rate (Attrition)
IDRes-EVAncillary EVMarket Potential | ID | Res-EV | Ancillary EV | Market Potential | % of Eligible Customers | 1.5% | 4.5% | 10.5% | 13.5% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | Assumption: One Third of TOU Demand Rate w EV. This participation rate will be throttled / scaled using the equipment saturation for EVs, which will be quite low. |  | 15% | 5 | 1% | Res-EVSteady State Participation Rate | Res-EVProgram ramp up period | Market PotentialID | Res-EVProgram Dropout Rate (Attrition)
IDRes-EVAncillary EVProgram Dropout Rate (Attrition) | ID | Res-EV | Ancillary EV | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Assumption: One Third of TOU Demand Rate w EV. This participation rate will be throttled / scaled using the equipment saturation for EVs, which will be quite low. |  | 15% | 5 | 1% | Res-EVSteady State Participation Rate | Res-EVProgram ramp up period | Market PotentialID | Res-EVProgram Dropout Rate (Attrition)
IDGS-EVAncillary EVMarket Potential | ID | GS-EV | Ancillary EV | Market Potential | % of Eligible Customers | 1.5% | 4.5% | 10.5% | 13.5% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | Prelim Assumption: One Third of EV TOU Demand Rate |  | 15% | 5 | 1% | GS-EVSteady State Participation Rate | GS-EVProgram ramp up period | Market PotentialID | GS-EVProgram Dropout Rate (Attrition)
IDGS-EVAncillary EVProgram Dropout Rate (Attrition) | ID | GS-EV | Ancillary EV | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Prelim Assumption: One Third of EV TOU Demand Rate |  | 15% | 5 | 1% | GS-EVSteady State Participation Rate | GS-EVProgram ramp up period | Market PotentialID | GS-EVProgram Dropout Rate (Attrition)
IDGeneral ServiceThird Party ContractsMarket Potential | ID | General Service | Third Party Contracts | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceThird Party ContractsProgram Dropout Rate (Attrition) | ID | General Service | Third Party Contracts | Program Dropout Rate (Attrition) | % | [30 empty] | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDLarge General ServiceThird Party ContractsMarket Potential | ID | Large General Service | Third Party Contracts | Market Potential | % of Eligible Customers | 7.5% | 12% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 2024 Avista Update |  | 15% | 3 | 1% | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialID | Large General ServiceProgram Dropout Rate (Attrition)
IDLarge General ServiceThird Party ContractsProgram Dropout Rate (Attrition) | ID | Large General Service | Third Party Contracts | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2024 Avista Update |  | 15% | 3 | 1% | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialID | Large General ServiceProgram Dropout Rate (Attrition)
IDExtra Large General ServiceThird Party ContractsMarket Potential | ID | Extra Large General Service | Third Party Contracts | Market Potential | % of Eligible Customers | 7.5% | 12% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 2024 Avista Update |  | 15% | 3 | 1% | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialID | Extra Large General ServiceProgram Dropout Rate (Attrition)
IDExtra Large General ServiceThird Party ContractsProgram Dropout Rate (Attrition) | ID | Extra Large General Service | Third Party Contracts | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2024 Avista Update |  | 15% | 3 | 1% | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialID | Extra Large General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceAncillary Third PartyMarket Potential | ID | General Service | Ancillary Third Party | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceAncillary Third PartyProgram Dropout Rate (Attrition) | ID | General Service | Ancillary Third Party | Program Dropout Rate (Attrition) | % | [30 empty] | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDLarge General ServiceAncillary Third PartyMarket Potential | ID | Large General Service | Ancillary Third Party | Market Potential | % of Eligible Customers | 1.08% | 1.728% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | Participation rate based on 2020 EE Study saturations of EMS systems within Avista commercial customers, weighted by segment size. |  | 2.16% | 3 | 1% | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialID | Large General ServiceProgram Dropout Rate (Attrition)
IDLarge General ServiceAncillary Third PartyProgram Dropout Rate (Attrition) | ID | Large General Service | Ancillary Third Party | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Participation rate based on 2020 EE Study saturations of EMS systems within Avista commercial customers, weighted by segment size. |  | 2.16% | 3 | 1% | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialID | Large General ServiceProgram Dropout Rate (Attrition)
IDExtra Large General ServiceAncillary Third PartyMarket Potential | ID | Extra Large General Service | Ancillary Third Party | Market Potential | % of Eligible Customers | 1.08% | 1.728% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | 2.16% | Participation rate based on 2020 EE Study saturations of EMS systems within Avista commercial customers, weighted by segment size. |  | 2.16% | 3 | 1% | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialID | Extra Large General ServiceProgram Dropout Rate (Attrition)
IDExtra Large General ServiceAncillary Third PartyProgram Dropout Rate (Attrition) | ID | Extra Large General Service | Ancillary Third Party | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Participation rate based on 2020 EE Study saturations of EMS systems within Avista commercial customers, weighted by segment size. |  | 2.16% | 3 | 1% | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialID | Extra Large General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceThermal Energy StorageMarket Potential | ID | General Service | Thermal Energy Storage | Market Potential | % of Eligible Customers | 0.05% | 0.15% | 0.35% | 0.45% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | Don't expect much participation - 0.5% |  | 0.5% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceThermal Energy StorageProgram Dropout Rate (Attrition) | ID | General Service | Thermal Energy Storage | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Don't expect much participation - 0.5% |  | 0.5% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDLarge General ServiceThermal Energy StorageMarket Potential | ID | Large General Service | Thermal Energy Storage | Market Potential | % of Eligible Customers | 0.15% | 0.45% | 1.05% | 1.35% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | Low participation is 1/2 DLC CAC |  | 1.5% | 5 | 1% | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialID | Large General ServiceProgram Dropout Rate (Attrition)
IDLarge General ServiceThermal Energy StorageProgram Dropout Rate (Attrition) | ID | Large General Service | Thermal Energy Storage | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Low participation is 1/2 DLC CAC |  | 1.5% | 5 | 1% | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialID | Large General ServiceProgram Dropout Rate (Attrition)
IDExtra Large General ServiceThermal Energy StorageMarket Potential | ID | Extra Large General Service | Thermal Energy Storage | Market Potential | % of Eligible Customers | 0.15% | 0.45% | 1.05% | 1.35% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | 1.5% | Low participation is 1/2 DLC CAC |  | 1.5% | 5 | 1% | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialID | Extra Large General ServiceProgram Dropout Rate (Attrition)
IDExtra Large General ServiceThermal Energy StorageProgram Dropout Rate (Attrition) | ID | Extra Large General Service | Thermal Energy Storage | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Low participation is 1/2 DLC CAC |  | 1.5% | 5 | 1% | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialID | Extra Large General ServiceProgram Dropout Rate (Attrition)
IDResidentialBattery Energy StorageMarket Potential | ID | Residential | Battery Energy Storage | Market Potential | % of Eligible Customers | 0.7436% | 2.231% | 5.206% | 6.693% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | PAC saw ~2.23% of solar PV customers participate in a battery DR program in year 2 of the program. (https://www.pacificorp.com/content/dam/pcorp/documents/en/pacificorp/environment/dsm/utah/2022_Utah_Wattsmart_Business_Energy_Eff_Peak_Reduction.pdf), solar PV # from DNV PG Study |  | 7.436% | 5 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialBattery Energy StorageProgram Dropout Rate (Attrition) | ID | Residential | Battery Energy Storage | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | PAC saw ~2.23% of solar PV customers participate in a battery DR program in year 2 of the program. (https://www.pacificorp.com/content/dam/pcorp/documents/en/pacificorp/environment/dsm/utah/2022_Utah_Wattsmart_Business_Energy_Eff_Peak_Reduction.pdf), solar PV # from DNV PG Study |  | 7.436% | 5 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServiceBattery Energy StorageMarket Potential | ID | General Service | Battery Energy Storage | Market Potential | % of Eligible Customers | 0.1487% | 0.2975% | 0.5949% | 0.8924% | 1.19% | 1.636% | 2.082% | 2.528% | 3.123% | 3.718% | 4.313% | 5.057% | 5.8% | 6.544% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | 7.436% | Same as Residential |  | 7.436% | 15 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceBattery Energy StorageProgram Dropout Rate (Attrition) | ID | General Service | Battery Energy Storage | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Same as Residential |  | 7.436% | 15 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDLarge General ServiceBattery Energy StorageMarket Potential | ID | Large General Service | Battery Energy Storage | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialID | Large General ServiceProgram Dropout Rate (Attrition)
IDLarge General ServiceBattery Energy StorageProgram Dropout Rate (Attrition) | ID | Large General Service | Battery Energy Storage | Program Dropout Rate (Attrition) | % | [30 empty] | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialID | Large General ServiceProgram Dropout Rate (Attrition)
IDExtra Large General ServiceBattery Energy StorageMarket Potential | ID | Extra Large General Service | Battery Energy Storage | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialID | Extra Large General ServiceProgram Dropout Rate (Attrition)
IDExtra Large General ServiceBattery Energy StorageProgram Dropout Rate (Attrition) | ID | Extra Large General Service | Battery Energy Storage | Program Dropout Rate (Attrition) | % | [30 empty] | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialID | Extra Large General ServiceProgram Dropout Rate (Attrition)
IDResidentialAncillary Battery StorageMarket Potential | ID | Residential | Ancillary Battery Storage | Market Potential | % of Eligible Customers | 0.01% | 0.02% | 0.04% | 0.06% | 0.08% | 0.11% | 0.14% | 0.17% | 0.21% | 0.25% | 0.29% | 0.34% | 0.39% | 0.44% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 20% from MISO LRZ 7. Assuming half for high and half again for low. *halved again 9-14-17, as per discussion with Kelly - potential looked too high. Pacificorp study didn't consider this program |  | 0.5% | 15 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialAncillary Battery StorageProgram Dropout Rate (Attrition) | ID | Residential | Ancillary Battery Storage | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 20% from MISO LRZ 7. Assuming half for high and half again for low. *halved again 9-14-17, as per discussion with Kelly - potential looked too high. Pacificorp study didn't consider this program |  | 0.5% | 15 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServiceAncillary Battery StorageMarket Potential | ID | General Service | Ancillary Battery Storage | Market Potential | % of Eligible Customers | 0.01% | 0.02% | 0.04% | 0.06% | 0.08% | 0.11% | 0.14% | 0.17% | 0.21% | 0.25% | 0.29% | 0.34% | 0.39% | 0.44% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | 0.5% | Same as Residential |  | 0.5% | 15 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceAncillary Battery StorageProgram Dropout Rate (Attrition) | ID | General Service | Ancillary Battery Storage | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Same as Residential |  | 0.5% | 15 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDLarge General ServiceAncillary Battery StorageMarket Potential | ID | Large General Service | Ancillary Battery Storage | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialID | Large General ServiceProgram Dropout Rate (Attrition)
IDLarge General ServiceAncillary Battery StorageProgram Dropout Rate (Attrition) | ID | Large General Service | Ancillary Battery Storage | Program Dropout Rate (Attrition) | % | [30 empty] | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialID | Large General ServiceProgram Dropout Rate (Attrition)
IDExtra Large General ServiceAncillary Battery StorageMarket Potential | ID | Extra Large General Service | Ancillary Battery Storage | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialID | Extra Large General ServiceProgram Dropout Rate (Attrition)
IDExtra Large General ServiceAncillary Battery StorageProgram Dropout Rate (Attrition) | ID | Extra Large General Service | Ancillary Battery Storage | Program Dropout Rate (Attrition) | % | [30 empty] | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialID | Extra Large General ServiceProgram Dropout Rate (Attrition)
IDResidentialBehavioralMarket Potential | ID | Residential | Behavioral | Market Potential | % of Eligible Customers | 10% | 16% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | high rate based on PG&E rollout with six waves http://www.calmac.org/publications/DNVGL_PGE_HERs_2015_final_to_calmac.pdf --> PC study has high case at 20% |  | 20% | 3 | 2% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialBehavioralProgram Dropout Rate (Attrition) | ID | Residential | Behavioral | Program Dropout Rate (Attrition) | % | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | high rate based on PG&E rollout with six waves http://www.calmac.org/publications/DNVGL_PGE_HERs_2015_final_to_calmac.pdf --> PC study has high case at 20% |  | 20% | 3 | 2% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialPilot-Time-of-Use Opt-inMarket Potential | ID | Residential | Pilot-Time-of-Use Opt-in | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified for pilot scope |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialPilot-Time-of-Use Opt-inProgram Dropout Rate (Attrition) | ID | Residential | Pilot-Time-of-Use Opt-in | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified for pilot scope |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServicePilot-Time-of-Use Opt-inMarket Potential | ID | General Service | Pilot-Time-of-Use Opt-in | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified for pilot scope |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServicePilot-Time-of-Use Opt-inProgram Dropout Rate (Attrition) | ID | General Service | Pilot-Time-of-Use Opt-in | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified for pilot scope |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDResidentialParent-Time-of-Use Opt-inMarket Potential | ID | Residential | Parent-Time-of-Use Opt-in | Market Potential | % of Eligible Customers | 1.3% | 3.9% | 9.1% | 11.7% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | 13% | Brattle Analysis and Estimate |  | 13% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialParent-Time-of-Use Opt-inProgram Dropout Rate (Attrition) | ID | Residential | Parent-Time-of-Use Opt-in | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | Brattle Analysis and Estimate |  | 13% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServiceParent-Time-of-Use Opt-inMarket Potential | ID | General Service | Parent-Time-of-Use Opt-in | Market Potential | % of Eligible Customers | 0.7% | 2.1% | 4.9% | 6.3% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 7% | 2024 Avista Update |  | 7% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceParent-Time-of-Use Opt-inProgram Dropout Rate (Attrition) | ID | General Service | Parent-Time-of-Use Opt-in | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2024 Avista Update |  | 7% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDLarge General ServiceParent-Time-of-Use Opt-inMarket Potential | ID | Large General Service | Parent-Time-of-Use Opt-in | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialID | Large General ServiceProgram Dropout Rate (Attrition)
IDLarge General ServiceParent-Time-of-Use Opt-inProgram Dropout Rate (Attrition) | ID | Large General Service | Parent-Time-of-Use Opt-in | Program Dropout Rate (Attrition) | % | [30 empty] | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialID | Large General ServiceProgram Dropout Rate (Attrition)
IDExtra Large General ServiceParent-Time-of-Use Opt-inMarket Potential | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialID | Extra Large General ServiceProgram Dropout Rate (Attrition)
IDExtra Large General ServiceParent-Time-of-Use Opt-inProgram Dropout Rate (Attrition) | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Program Dropout Rate (Attrition) | % | [30 empty] | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialID | Extra Large General ServiceProgram Dropout Rate (Attrition)
IDResidentialTime-of-Use Opt-OutMarket Potential | ID | Residential | Time-of-Use Opt-Out | Market Potential | % of Eligible Customers | 100% | 85.4% | 78.9% | 75.6% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 2024 Avista Update |  | 20% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialTime-of-Use Opt-OutProgram Dropout Rate (Attrition) | ID | Residential | Time-of-Use Opt-Out | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2024 Avista Update |  | 20% | 5 | 1% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServiceTime-of-Use Opt-OutMarket Potential | ID | General Service | Time-of-Use Opt-Out | Market Potential | % of Eligible Customers | 100% | 85.4% | 78.9% | 75.6% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 2024 Avista Update |  | 20% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceTime-of-Use Opt-OutProgram Dropout Rate (Attrition) | ID | General Service | Time-of-Use Opt-Out | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2024 Avista Update |  | 20% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDLarge General ServiceTime-of-Use Opt-OutMarket Potential | ID | Large General Service | Time-of-Use Opt-Out | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialID | Large General ServiceProgram Dropout Rate (Attrition)
IDLarge General ServiceTime-of-Use Opt-OutProgram Dropout Rate (Attrition) | ID | Large General Service | Time-of-Use Opt-Out | Program Dropout Rate (Attrition) | % | [30 empty] | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialID | Large General ServiceProgram Dropout Rate (Attrition)
IDExtra Large General ServiceTime-of-Use Opt-OutMarket Potential | ID | Extra Large General Service | Time-of-Use Opt-Out | Market Potential | % of Eligible Customers | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | #VALUE! | [5 empty] | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialID | Extra Large General ServiceProgram Dropout Rate (Attrition)
IDExtra Large General ServiceTime-of-Use Opt-OutProgram Dropout Rate (Attrition) | ID | Extra Large General Service | Time-of-Use Opt-Out | Program Dropout Rate (Attrition) | % | [30 empty] | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialID | Extra Large General ServiceProgram Dropout Rate (Attrition)
IDGS-EVElectric Vehicle TOU Opt-inMarket Potential | ID | GS-EV | Electric Vehicle TOU Opt-in | Market Potential | % of Eligible Customers | 2% | 6% | 14% | 18% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 2024 Avista Update: sch 13 |  | 20% | 5 | 1% | GS-EVSteady State Participation Rate | GS-EVProgram ramp up period | Market PotentialID | GS-EVProgram Dropout Rate (Attrition)
IDGS-EVElectric Vehicle TOU Opt-inProgram Dropout Rate (Attrition) | ID | GS-EV | Electric Vehicle TOU Opt-in | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2024 Avista Update: sch 13 |  | 20% | 5 | 1% | GS-EVSteady State Participation Rate | GS-EVProgram ramp up period | Market PotentialID | GS-EVProgram Dropout Rate (Attrition)
IDLGS-EVElectric Vehicle TOU Opt-inMarket Potential | ID | LGS-EV | Electric Vehicle TOU Opt-in | Market Potential | % of Eligible Customers | 1% | 3% | 7% | 9% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 2024 Avista Update: sch 23 |  | 10% | 5 | 1% | LGS-EVSteady State Participation Rate | LGS-EVProgram ramp up period | Market PotentialID | LGS-EVProgram Dropout Rate (Attrition)
IDLGS-EVElectric Vehicle TOU Opt-inProgram Dropout Rate (Attrition) | ID | LGS-EV | Electric Vehicle TOU Opt-in | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 2024 Avista Update: sch 23 |  | 10% | 5 | 1% | LGS-EVSteady State Participation Rate | LGS-EVProgram ramp up period | Market PotentialID | LGS-EVProgram Dropout Rate (Attrition)
IDResidentialParent-Peak Time RebateMarket Potential | ID | Residential | Parent-Peak Time Rebate | Market Potential | % of Eligible Customers | 1.5% | 4.5% | 10.5% | 13.5% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: Goal of 110,000 out of ~800,000 residential customers (see table below) |  | 15% | 5 | 2% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialParent-Peak Time RebateProgram Dropout Rate (Attrition) | ID | Residential | Parent-Peak Time Rebate | Program Dropout Rate (Attrition) | % | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: Goal of 110,000 out of ~800,000 residential customers (see table below) |  | 15% | 5 | 2% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServiceParent-Peak Time RebateMarket Potential | ID | General Service | Parent-Peak Time Rebate | Market Potential | % of Eligible Customers | 1.5% | 4.5% | 10.5% | 13.5% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | 15% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: Goal of 110,000 out of ~800,000 residential customers (see table below) |  | 15% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServiceParent-Peak Time RebateProgram Dropout Rate (Attrition) | ID | General Service | Parent-Peak Time Rebate | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: Goal of 110,000 out of ~800,000 residential customers (see table below) |  | 15% | 5 | 1% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDResidentialPilot-Peak Time RebateMarket Potential | ID | Residential | Pilot-Peak Time Rebate | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified for pilot scope |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDResidentialPilot-Peak Time RebateProgram Dropout Rate (Attrition) | ID | Residential | Pilot-Peak Time Rebate | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified for pilot scope |  | 0% | 0 | 0% | ResidentialSteady State Participation Rate | ResidentialProgram ramp up period | Market PotentialID | ResidentialProgram Dropout Rate (Attrition)
IDGeneral ServicePilot-Peak Time RebateMarket Potential | ID | General Service | Pilot-Peak Time Rebate | Market Potential | % of Eligible Customers | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified for pilot scope |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDGeneral ServicePilot-Peak Time RebateProgram Dropout Rate (Attrition) | ID | General Service | Pilot-Peak Time Rebate | Program Dropout Rate (Attrition) | % | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Modified for pilot scope |  | 0% | 0 | 0% | General ServiceSteady State Participation Rate | General ServiceProgram ramp up period | Market PotentialID | General ServiceProgram Dropout Rate (Attrition)
IDLarge General ServiceVariable Peak Pricing RatesMarket Potential | ID | Large General Service | Variable Peak Pricing Rates | Market Potential | % of Eligible Customers | 2.5% | 7.5% | 17.5% | 22.5% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | High Case- OG&E's VPP Plus participation rate- should be 103000/400000 around 25% |  | 25% | 5 | 1% | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialID | Large General ServiceProgram Dropout Rate (Attrition)
IDLarge General ServiceVariable Peak Pricing RatesProgram Dropout Rate (Attrition) | ID | Large General Service | Variable Peak Pricing Rates | Program Dropout Rate (Attrition) | % | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | 1% | High Case- OG&E's VPP Plus participation rate- should be 103000/400000 around 25% |  | 25% | 5 | 1% | Large General ServiceSteady State Participation Rate | Large General ServiceProgram ramp up period | Market PotentialID | Large General ServiceProgram Dropout Rate (Attrition)
IDExtra Large General ServiceVariable Peak Pricing RatesMarket Potential | ID | Extra Large General Service | Variable Peak Pricing Rates | Market Potential | % of Eligible Customers | 2.5% | 7.5% | 17.5% | 22.5% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | 25% | High Case- OG&E's VPP Plus participation rate |  | 25% | 5 | 2% | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialID | Extra Large General ServiceProgram Dropout Rate (Attrition)
IDExtra Large General ServiceVariable Peak Pricing RatesProgram Dropout Rate (Attrition) | ID | Extra Large General Service | Variable Peak Pricing Rates | Program Dropout Rate (Attrition) | % | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | High Case- OG&E's VPP Plus participation rate |  | 25% | 5 | 2% | Extra Large General ServiceSteady State Participation Rate | Extra Large General ServiceProgram ramp up period | Market PotentialID | Extra Large General ServiceProgram Dropout Rate (Attrition)
Note on AR19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Modified ramp for CTA ERWH parent to be consistent with pilot
Note on AR30: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Modified 3-year ramp for PTR pilot program. Reply: Switched TOU pilot to modifed 3-year ramp.
Note on AR31: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Modified 5-year ramp for TOU pilot program.

## ImpactInput
Key | State | Customer Class | Option | Data Element | Unit | Market Potential | Comments from Input Generator | Copy & Paste Values to Left into Model |  | Row Lookup | Column Lookup
WAResidentialDLC Central ACEvent Non-Performance Rate | WA | Residential | DLC Central AC | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialDLC Central ACPer Customer Summer Peak Reduction (kW) | WA | Residential | DLC Central AC | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.5 | NWPC DLC Switch cooling assumption (east) |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialDLC Central ACPer Customer Summer Peak Reduction (%) | WA | Residential | DLC Central AC | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialDLC Central ACPer Customer Winter Peak Reduction (kW) | WA | Residential | DLC Central AC | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialDLC Central ACPer Customer Winter Peak Reduction (%) | WA | Residential | DLC Central AC | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceDLC Central ACEvent Non-Performance Rate | WA | General Service | DLC Central AC | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceDLC Central ACPer Customer Summer Peak Reduction (kW) | WA | General Service | DLC Central AC | Per Customer Summer Peak Reduction (kW) | kW @meter | 1.25 | NWPC DLC Switch cooling assumption (East) |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceDLC Central ACPer Customer Summer Peak Reduction (%) | WA | General Service | DLC Central AC | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceDLC Central ACPer Customer Winter Peak Reduction (kW) | WA | General Service | DLC Central AC | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceDLC Central ACPer Customer Winter Peak Reduction (%) | WA | General Service | DLC Central AC | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingEvent Non-Performance Rate | WA | Residential | DLC Smart Thermostats - Cooling | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingPer Customer Summer Peak Reduction (kW) | WA | Residential | DLC Smart Thermostats - Cooling | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.5 | NWPC DLC Switch cooling assumption (east)- Thermostat impact was 1.27 kW but didn't seem right so we defaulted to DLC Central AC |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingPer Customer Summer Peak Reduction (%) | WA | Residential | DLC Smart Thermostats - Cooling | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingPer Customer Winter Peak Reduction (kW) | WA | Residential | DLC Smart Thermostats - Cooling | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingPer Customer Winter Peak Reduction (%) | WA | Residential | DLC Smart Thermostats - Cooling | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingEvent Non-Performance Rate | WA | General Service | DLC Smart Thermostats - Cooling | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingPer Customer Summer Peak Reduction (kW) | WA | General Service | DLC Smart Thermostats - Cooling | Per Customer Summer Peak Reduction (kW) | kW @meter | 1.25 | NWPC DLC Switch cooling assumption (East) |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingPer Customer Summer Peak Reduction (%) | WA | General Service | DLC Smart Thermostats - Cooling | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingPer Customer Winter Peak Reduction (kW) | WA | General Service | DLC Smart Thermostats - Cooling | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingPer Customer Winter Peak Reduction (%) | WA | General Service | DLC Smart Thermostats - Cooling | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialAncillary CoolingEvent Non-Performance Rate | WA | Residential | Ancillary Cooling | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialAncillary CoolingPer Customer Summer Peak Reduction (kW) | WA | Residential | Ancillary Cooling | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.25 | Half of parent thermostat impact for ancillary |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialAncillary CoolingPer Customer Summer Peak Reduction (%) | WA | Residential | Ancillary Cooling | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialAncillary CoolingPer Customer Winter Peak Reduction (kW) | WA | Residential | Ancillary Cooling | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialAncillary CoolingPer Customer Winter Peak Reduction (%) | WA | Residential | Ancillary Cooling | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceAncillary CoolingEvent Non-Performance Rate | WA | General Service | Ancillary Cooling | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceAncillary CoolingPer Customer Summer Peak Reduction (kW) | WA | General Service | Ancillary Cooling | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.625 | NWPC DLC Switch cooling assumption (East)- Half impact for ancillary |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceAncillary CoolingPer Customer Summer Peak Reduction (%) | WA | General Service | Ancillary Cooling | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceAncillary CoolingPer Customer Winter Peak Reduction (kW) | WA | General Service | Ancillary Cooling | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceAncillary CoolingPer Customer Winter Peak Reduction (%) | WA | General Service | Ancillary Cooling | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingEvent Non-Performance Rate | WA | Residential | DLC Smart Thermostats - Heating | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingPer Customer Summer Peak Reduction (kW) | WA | Residential | DLC Smart Thermostats - Heating | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingPer Customer Summer Peak Reduction (%) | WA | Residential | DLC Smart Thermostats - Heating | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingPer Customer Winter Peak Reduction (kW) | WA | Residential | DLC Smart Thermostats - Heating | Per Customer Winter Peak Reduction (kW) | kW @meter | 1.09 | NWPC Smart thermostat heating assumption- general service uses 0.54 (switch to thermostat impact ratio) of eastern switch impact |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingPer Customer Winter Peak Reduction (%) | WA | Residential | DLC Smart Thermostats - Heating | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingEvent Non-Performance Rate | WA | General Service | DLC Smart Thermostats - Heating | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingPer Customer Summer Peak Reduction (kW) | WA | General Service | DLC Smart Thermostats - Heating | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingPer Customer Summer Peak Reduction (%) | WA | General Service | DLC Smart Thermostats - Heating | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingPer Customer Winter Peak Reduction (kW) | WA | General Service | DLC Smart Thermostats - Heating | Per Customer Winter Peak Reduction (kW) | kW @meter | 1.35 | NWPC Smart thermostat heating assumption- general service uses 0.54 (switch to thermostat impact ratio) of eastern switch impact of 2.5 |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingPer Customer Winter Peak Reduction (%) | WA | General Service | DLC Smart Thermostats - Heating | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialAncillary HeatingEvent Non-Performance Rate | WA | Residential | Ancillary Heating | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialAncillary HeatingPer Customer Summer Peak Reduction (kW) | WA | Residential | Ancillary Heating | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialAncillary HeatingPer Customer Summer Peak Reduction (%) | WA | Residential | Ancillary Heating | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialAncillary HeatingPer Customer Winter Peak Reduction (kW) | WA | Residential | Ancillary Heating | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.545 | Half of Smart Thermostat Heating Per-Customer Impact |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialAncillary HeatingPer Customer Winter Peak Reduction (%) | WA | Residential | Ancillary Heating | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceAncillary HeatingEvent Non-Performance Rate | WA | General Service | Ancillary Heating | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceAncillary HeatingPer Customer Summer Peak Reduction (kW) | WA | General Service | Ancillary Heating | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceAncillary HeatingPer Customer Summer Peak Reduction (%) | WA | General Service | Ancillary Heating | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceAncillary HeatingPer Customer Winter Peak Reduction (kW) | WA | General Service | Ancillary Heating | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.675 | Half of parent Smart Thermostat-Heating per-customer impacts |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceAncillary HeatingPer Customer Winter Peak Reduction (%) | WA | General Service | Ancillary Heating | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialDLC Water HeatingEvent Non-Performance Rate | WA | Residential | DLC Water Heating | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialDLC Water HeatingPer Customer Summer Peak Reduction (kW) | WA | Residential | DLC Water Heating | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Switch Summer Impact, derated to align with Wh proportion of peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialDLC Water HeatingPer Customer Summer Peak Reduction (%) | WA | Residential | DLC Water Heating | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialDLC Water HeatingPer Customer Winter Peak Reduction (kW) | WA | Residential | DLC Water Heating | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Switch Winter Impact, derated to align with Wh proportion of peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialDLC Water HeatingPer Customer Winter Peak Reduction (%) | WA | Residential | DLC Water Heating | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceDLC Water HeatingEvent Non-Performance Rate | WA | General Service | DLC Water Heating | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceDLC Water HeatingPer Customer Summer Peak Reduction (kW) | WA | General Service | DLC Water Heating | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 7th Plan, pg 25 from Cadmnus Report, Commercial: Res value multiplied by the CAC DLC ratio (small C&I impact /Res impact) |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceDLC Water HeatingPer Customer Summer Peak Reduction (%) | WA | General Service | DLC Water Heating | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceDLC Water HeatingPer Customer Winter Peak Reduction (kW) | WA | General Service | DLC Water Heating | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 7th Plan, pg 25 from Cadmnus Report, Commercial: Res value multiplied by the CAC DLC ratio (small C&I impact /Res impact) |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceDLC Water HeatingPer Customer Winter Peak Reduction (%) | WA | General Service | DLC Water Heating | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialAncillary DLC WHEvent Non-Performance Rate | WA | Residential | Ancillary DLC WH | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialAncillary DLC WHPer Customer Summer Peak Reduction (kW) | WA | Residential | Ancillary DLC WH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Switch Summer Impact, derated to align with Wh proportion of peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialAncillary DLC WHPer Customer Summer Peak Reduction (%) | WA | Residential | Ancillary DLC WH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialAncillary DLC WHPer Customer Winter Peak Reduction (kW) | WA | Residential | Ancillary DLC WH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Switch Winter Impact, derated to align with Wh proportion of peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialAncillary DLC WHPer Customer Winter Peak Reduction (%) | WA | Residential | Ancillary DLC WH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceAncillary DLC WHEvent Non-Performance Rate | WA | General Service | Ancillary DLC WH | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceAncillary DLC WHPer Customer Summer Peak Reduction (kW) | WA | General Service | Ancillary DLC WH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 7th Plan, pg 25 from Cadmnus Report, Commercial: Res value multiplied by the CAC DLC ratio (small C&I impact /Res impact) |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceAncillary DLC WHPer Customer Summer Peak Reduction (%) | WA | General Service | Ancillary DLC WH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceAncillary DLC WHPer Customer Winter Peak Reduction (kW) | WA | General Service | Ancillary DLC WH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 7th Plan, pg 25 from Cadmnus Report, Commercial: Res value multiplied by the CAC DLC ratio (small C&I impact /Res impact) |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceAncillary DLC WHPer Customer Winter Peak Reduction (%) | WA | General Service | Ancillary DLC WH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHEvent Non-Performance Rate | WA | Residential | Pilot-CTA-2045 HPWH | Event Non-Performance Rate | % | 3% | Ability for customers to easily override event- using 3% as placeholder |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHPer Customer Summer Peak Reduction (kW) | WA | Residential | Pilot-CTA-2045 HPWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.09 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHPer Customer Summer Peak Reduction (%) | WA | Residential | Pilot-CTA-2045 HPWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHPer Customer Winter Peak Reduction (kW) | WA | Residential | Pilot-CTA-2045 HPWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.14 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHPer Customer Winter Peak Reduction (%) | WA | Residential | Pilot-CTA-2045 HPWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHEvent Non-Performance Rate | WA | General Service | Pilot-CTA-2045 HPWH | Event Non-Performance Rate | % | 3% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHPer Customer Summer Peak Reduction (kW) | WA | General Service | Pilot-CTA-2045 HPWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.225 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHPer Customer Summer Peak Reduction (%) | WA | General Service | Pilot-CTA-2045 HPWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHPer Customer Winter Peak Reduction (kW) | WA | General Service | Pilot-CTA-2045 HPWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.35 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHPer Customer Winter Peak Reduction (%) | WA | General Service | Pilot-CTA-2045 HPWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHEvent Non-Performance Rate | WA | Residential | Parent-CTA-2045 HPWH | Event Non-Performance Rate | % | 3% | Ability for customers to easily override event- using 3% as placeholder |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHPer Customer Summer Peak Reduction (kW) | WA | Residential | Parent-CTA-2045 HPWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.09 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHPer Customer Summer Peak Reduction (%) | WA | Residential | Parent-CTA-2045 HPWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHPer Customer Winter Peak Reduction (kW) | WA | Residential | Parent-CTA-2045 HPWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.14 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHPer Customer Winter Peak Reduction (%) | WA | Residential | Parent-CTA-2045 HPWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHEvent Non-Performance Rate | WA | General Service | Parent-CTA-2045 HPWH | Event Non-Performance Rate | % | 3% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHPer Customer Summer Peak Reduction (kW) | WA | General Service | Parent-CTA-2045 HPWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.225 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHPer Customer Summer Peak Reduction (%) | WA | General Service | Parent-CTA-2045 HPWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHPer Customer Winter Peak Reduction (kW) | WA | General Service | Parent-CTA-2045 HPWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.35 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.56x of res |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHPer Customer Winter Peak Reduction (%) | WA | General Service | Parent-CTA-2045 HPWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialPilot-Ancillary HPWHEvent Non-Performance Rate | WA | Residential | Pilot-Ancillary HPWH | Event Non-Performance Rate | % | 3% | Ability for customers to easily override event- using 3% as placeholder |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialPilot-Ancillary HPWHPer Customer Summer Peak Reduction (kW) | WA | Residential | Pilot-Ancillary HPWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.09 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialPilot-Ancillary HPWHPer Customer Summer Peak Reduction (%) | WA | Residential | Pilot-Ancillary HPWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialPilot-Ancillary HPWHPer Customer Winter Peak Reduction (kW) | WA | Residential | Pilot-Ancillary HPWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.14 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialPilot-Ancillary HPWHPer Customer Winter Peak Reduction (%) | WA | Residential | Pilot-Ancillary HPWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHEvent Non-Performance Rate | WA | General Service | Pilot-Ancillary HPWH | Event Non-Performance Rate | % | 3% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHPer Customer Summer Peak Reduction (kW) | WA | General Service | Pilot-Ancillary HPWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.225 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHPer Customer Summer Peak Reduction (%) | WA | General Service | Pilot-Ancillary HPWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHPer Customer Winter Peak Reduction (kW) | WA | General Service | Pilot-Ancillary HPWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.35 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHPer Customer Winter Peak Reduction (%) | WA | General Service | Pilot-Ancillary HPWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialParent-Ancillary HPWHEvent Non-Performance Rate | WA | Residential | Parent-Ancillary HPWH | Event Non-Performance Rate | % | 3% | Ability for customers to easily override event- using 3% as placeholder |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialParent-Ancillary HPWHPer Customer Summer Peak Reduction (kW) | WA | Residential | Parent-Ancillary HPWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.09 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialParent-Ancillary HPWHPer Customer Summer Peak Reduction (%) | WA | Residential | Parent-Ancillary HPWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialParent-Ancillary HPWHPer Customer Winter Peak Reduction (kW) | WA | Residential | Parent-Ancillary HPWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.14 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialParent-Ancillary HPWHPer Customer Winter Peak Reduction (%) | WA | Residential | Parent-Ancillary HPWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHEvent Non-Performance Rate | WA | General Service | Parent-Ancillary HPWH | Event Non-Performance Rate | % | 3% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHPer Customer Summer Peak Reduction (kW) | WA | General Service | Parent-Ancillary HPWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.225 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHPer Customer Summer Peak Reduction (%) | WA | General Service | Parent-Ancillary HPWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHPer Customer Winter Peak Reduction (kW) | WA | General Service | Parent-Ancillary HPWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.35 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHPer Customer Winter Peak Reduction (%) | WA | General Service | Parent-Ancillary HPWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHEvent Non-Performance Rate | WA | Residential | Pilot-CTA-2045 ERWH | Event Non-Performance Rate | % | 3% | Ability for customers to easily override event- using 3% as placeholder |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHPer Customer Summer Peak Reduction (kW) | WA | Residential | Pilot-CTA-2045 ERWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.16 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH proportion of peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHPer Customer Summer Peak Reduction (%) | WA | Residential | Pilot-CTA-2045 ERWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHPer Customer Winter Peak Reduction (kW) | WA | Residential | Pilot-CTA-2045 ERWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.37 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Winter AM impact, derated to align with WH proportion of peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHPer Customer Winter Peak Reduction (%) | WA | Residential | Pilot-CTA-2045 ERWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHEvent Non-Performance Rate | WA | General Service | Pilot-CTA-2045 ERWH | Event Non-Performance Rate | % | 3% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHPer Customer Summer Peak Reduction (kW) | WA | General Service | Pilot-CTA-2045 ERWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.4 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHPer Customer Summer Peak Reduction (%) | WA | General Service | Pilot-CTA-2045 ERWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHPer Customer Winter Peak Reduction (kW) | WA | General Service | Pilot-CTA-2045 ERWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.925 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHPer Customer Winter Peak Reduction (%) | WA | General Service | Pilot-CTA-2045 ERWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHEvent Non-Performance Rate | WA | Residential | Parent-CTA-2045 ERWH | Event Non-Performance Rate | % | 3% | Ability for customers to easily override event- using 3% as placeholder |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHPer Customer Summer Peak Reduction (kW) | WA | Residential | Parent-CTA-2045 ERWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.16 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH proportion of peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHPer Customer Summer Peak Reduction (%) | WA | Residential | Parent-CTA-2045 ERWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHPer Customer Winter Peak Reduction (kW) | WA | Residential | Parent-CTA-2045 ERWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.37 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Winter AM impact, derated to align with WH proportion of peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHPer Customer Winter Peak Reduction (%) | WA | Residential | Parent-CTA-2045 ERWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHEvent Non-Performance Rate | WA | General Service | Parent-CTA-2045 ERWH | Event Non-Performance Rate | % | 3% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHPer Customer Summer Peak Reduction (kW) | WA | General Service | Parent-CTA-2045 ERWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.4 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHPer Customer Summer Peak Reduction (%) | WA | General Service | Parent-CTA-2045 ERWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHPer Customer Winter Peak Reduction (kW) | WA | General Service | Parent-CTA-2045 ERWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.925 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHPer Customer Winter Peak Reduction (%) | WA | General Service | Parent-CTA-2045 ERWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialPilot-Ancillary ERWHEvent Non-Performance Rate | WA | Residential | Pilot-Ancillary ERWH | Event Non-Performance Rate | % | 3% | Ability for customers to easily override event- using 3% as placeholder |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialPilot-Ancillary ERWHPer Customer Summer Peak Reduction (kW) | WA | Residential | Pilot-Ancillary ERWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.16 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH proportion of peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialPilot-Ancillary ERWHPer Customer Summer Peak Reduction (%) | WA | Residential | Pilot-Ancillary ERWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialPilot-Ancillary ERWHPer Customer Winter Peak Reduction (kW) | WA | Residential | Pilot-Ancillary ERWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.37 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Winter AM impact, derated to align with WH proportion of peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialPilot-Ancillary ERWHPer Customer Winter Peak Reduction (%) | WA | Residential | Pilot-Ancillary ERWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHEvent Non-Performance Rate | WA | General Service | Pilot-Ancillary ERWH | Event Non-Performance Rate | % | 3% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHPer Customer Summer Peak Reduction (kW) | WA | General Service | Pilot-Ancillary ERWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.4 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHPer Customer Summer Peak Reduction (%) | WA | General Service | Pilot-Ancillary ERWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHPer Customer Winter Peak Reduction (kW) | WA | General Service | Pilot-Ancillary ERWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.925 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHPer Customer Winter Peak Reduction (%) | WA | General Service | Pilot-Ancillary ERWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialParent-Ancillary ERWHEvent Non-Performance Rate | WA | Residential | Parent-Ancillary ERWH | Event Non-Performance Rate | % | 3% | Ability for customers to easily override event- using 3% as placeholder |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialParent-Ancillary ERWHPer Customer Summer Peak Reduction (kW) | WA | Residential | Parent-Ancillary ERWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.16 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH proportion of peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialParent-Ancillary ERWHPer Customer Summer Peak Reduction (%) | WA | Residential | Parent-Ancillary ERWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialParent-Ancillary ERWHPer Customer Winter Peak Reduction (kW) | WA | Residential | Parent-Ancillary ERWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.37 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Winter AM impact, derated to align with WH proportion of peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialParent-Ancillary ERWHPer Customer Winter Peak Reduction (%) | WA | Residential | Parent-Ancillary ERWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHEvent Non-Performance Rate | WA | General Service | Parent-Ancillary ERWH | Event Non-Performance Rate | % | 3% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHPer Customer Summer Peak Reduction (kW) | WA | General Service | Parent-Ancillary ERWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.4 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHPer Customer Summer Peak Reduction (%) | WA | General Service | Parent-Ancillary ERWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHPer Customer Winter Peak Reduction (kW) | WA | General Service | Parent-Ancillary ERWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.925 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHPer Customer Winter Peak Reduction (%) | WA | General Service | Parent-Ancillary ERWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialDLC Smart AppliancesEvent Non-Performance Rate | WA | Residential | DLC Smart Appliances | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialDLC Smart AppliancesPer Customer Summer Peak Reduction (kW) | WA | Residential | DLC Smart Appliances | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.14 | Ghatikar, Rish. Demand Response Automation in Appliance and Equipment. Lawrence Berkley National Laboratory, 2015. Web. http://docketpublic.energy.ca.gov/PublicDocuments/15-IEPR-05/TN205072_20150618T110004_Demand_Response_Automation_in_Appliances_and_Equipment.pptx kw @ meter values= 0.14 for summer and winter |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialDLC Smart AppliancesPer Customer Summer Peak Reduction (%) | WA | Residential | DLC Smart Appliances | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialDLC Smart AppliancesPer Customer Winter Peak Reduction (kW) | WA | Residential | DLC Smart Appliances | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.14 | Ghatikar, Rish. Demand Response Automation in Appliance and Equipment. Lawrence Berkley National Laboratory, 2015. Web. http://docketpublic.energy.ca.gov/PublicDocuments/15-IEPR-05/TN205072_20150618T110004_Demand_Response_Automation_in_Appliances_and_Equipment.pptx kw @ meter values= 0.14 for summer and winter |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialDLC Smart AppliancesPer Customer Winter Peak Reduction (%) | WA | Residential | DLC Smart Appliances | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesEvent Non-Performance Rate | WA | General Service | DLC Smart Appliances | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesPer Customer Summer Peak Reduction (kW) | WA | General Service | DLC Smart Appliances | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.14 | Ghatikar, Rish. Demand Response Automation in Appliance and Equipment. Lawrence Berkley National Laboratory, 2015. Web. http://docketpublic.energy.ca.gov/PublicDocuments/15-IEPR-05/TN205072_20150618T110004_Demand_Response_Automation_in_Appliances_and_Equipment.pptx kw @ meter values= 0.14 for summer and winter |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesPer Customer Summer Peak Reduction (%) | WA | General Service | DLC Smart Appliances | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesPer Customer Winter Peak Reduction (kW) | WA | General Service | DLC Smart Appliances | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.14 | Ghatikar, Rish. Demand Response Automation in Appliance and Equipment. Lawrence Berkley National Laboratory, 2015. Web. http://docketpublic.energy.ca.gov/PublicDocuments/15-IEPR-05/TN205072_20150618T110004_Demand_Response_Automation_in_Appliances_and_Equipment.pptx kw @ meter values= 0.14 for summer and winter |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesPer Customer Winter Peak Reduction (%) | WA | General Service | DLC Smart Appliances | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingEvent Non-Performance Rate | WA | Res-EV | DLC Electric Vehicle Charging | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Res-EVEvent Non-Performance Rate | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingPer Customer Summer Peak Reduction (kW) | WA | Res-EV | DLC Electric Vehicle Charging | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | Update: Avista 2019 EVSE report claims 75% charging load reduction. Impact based on Res-EV impact/customer. OLD: Based on Avista research, expecting a 90% + Load Shift (0.5 kW) |  | 1 | Res-EVPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingPer Customer Summer Peak Reduction (%) | WA | Res-EV | DLC Electric Vehicle Charging | Per Customer Summer Peak Reduction (%) | % of Peak | 90% | 2024 Avista Update |  | 1 | Res-EVPer Customer Summer Peak Reduction (%) | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingPer Customer Winter Peak Reduction (kW) | WA | Res-EV | DLC Electric Vehicle Charging | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | Update: Avista 2019 EVSE report claims 75% charging load reduction. Impact based on Res-EV impact/customer. OLD: Based on Avista research, expecting a 90% + Load Shift (0.5 kW) |  | 1 | Res-EVPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingPer Customer Winter Peak Reduction (%) | WA | Res-EV | DLC Electric Vehicle Charging | Per Customer Winter Peak Reduction (%) | % of Peak | 90% | 2024 Avista Update |  | 1 | Res-EVPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingEvent Non-Performance Rate | WA | GS-EV | DLC Electric Vehicle Charging | Event Non-Performance Rate | % |  |  |  | 1 | GS-EVEvent Non-Performance Rate | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingPer Customer Summer Peak Reduction (kW) | WA | GS-EV | DLC Electric Vehicle Charging | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | GS-EVPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingPer Customer Summer Peak Reduction (%) | WA | GS-EV | DLC Electric Vehicle Charging | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | GS-EVPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingPer Customer Winter Peak Reduction (kW) | WA | GS-EV | DLC Electric Vehicle Charging | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | GS-EVPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingPer Customer Winter Peak Reduction (%) | WA | GS-EV | DLC Electric Vehicle Charging | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | GS-EVPer Customer Winter Peak Reduction (%) | Market PotentialWA
WARes-EVAncillary EVEvent Non-Performance Rate | WA | Res-EV | Ancillary EV | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Res-EVEvent Non-Performance Rate | Market PotentialWA
WARes-EVAncillary EVPer Customer Summer Peak Reduction (kW) | WA | Res-EV | Ancillary EV | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.25 | Half of parent impact for ancillary |  | 1 | Res-EVPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WARes-EVAncillary EVPer Customer Summer Peak Reduction (%) | WA | Res-EV | Ancillary EV | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | Res-EVPer Customer Summer Peak Reduction (%) | Market PotentialWA
WARes-EVAncillary EVPer Customer Winter Peak Reduction (kW) | WA | Res-EV | Ancillary EV | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.25 | Half of parent impact for ancillary |  | 1 | Res-EVPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WARes-EVAncillary EVPer Customer Winter Peak Reduction (%) | WA | Res-EV | Ancillary EV | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | Res-EVPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGS-EVAncillary EVEvent Non-Performance Rate | WA | GS-EV | Ancillary EV | Event Non-Performance Rate | % | 0% | 0 |  | 1 | GS-EVEvent Non-Performance Rate | Market PotentialWA
WAGS-EVAncillary EVPer Customer Summer Peak Reduction (kW) | WA | GS-EV | Ancillary EV | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | Update: Avista 2019 EVSE report claims 75% charging load reduction. Impact based on Res-EV impact/customer. OLD: Based on Avista research, expecting a 90% + Load Shift (0.5 kW) |  | 1 | GS-EVPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGS-EVAncillary EVPer Customer Summer Peak Reduction (%) | WA | GS-EV | Ancillary EV | Per Customer Summer Peak Reduction (%) | % of Peak | 75% | 0 |  | 1 | GS-EVPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGS-EVAncillary EVPer Customer Winter Peak Reduction (kW) | WA | GS-EV | Ancillary EV | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | Update: Avista 2019 EVSE report claims 75% charging load reduction. Impact based on Res-EV impact/customer. OLD: Based on Avista research, expecting a 90% + Load Shift (0.5 kW) |  | 1 | GS-EVPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGS-EVAncillary EVPer Customer Winter Peak Reduction (%) | WA | GS-EV | Ancillary EV | Per Customer Winter Peak Reduction (%) | % of Peak | 75% | 0 |  | 1 | GS-EVPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceThird Party ContractsEvent Non-Performance Rate | WA | General Service | Third Party Contracts | Event Non-Performance Rate | % |  |  |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceThird Party ContractsPer Customer Summer Peak Reduction (kW) | WA | General Service | Third Party Contracts | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceThird Party ContractsPer Customer Summer Peak Reduction (%) | WA | General Service | Third Party Contracts | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceThird Party ContractsPer Customer Winter Peak Reduction (kW) | WA | General Service | Third Party Contracts | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceThird Party ContractsPer Customer Winter Peak Reduction (%) | WA | General Service | Third Party Contracts | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WALarge General ServiceThird Party ContractsEvent Non-Performance Rate | WA | Large General Service | Third Party Contracts | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Large General ServiceEvent Non-Performance Rate | Market PotentialWA
WALarge General ServiceThird Party ContractsPer Customer Summer Peak Reduction (kW) | WA | Large General Service | Third Party Contracts | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WALarge General ServiceThird Party ContractsPer Customer Summer Peak Reduction (%) | WA | Large General Service | Third Party Contracts | Per Customer Summer Peak Reduction (%) | % of Peak | 21% | weighted average from impacts in the following report: Impact Estimates from Aggregator Programs in California (Source: 2012 Statewide Load Impact Evaluation of California Aggregator Demand Response Programs Volume 1: Ex post and Ex ante Load Impacts; Christensen Associates Energy Consulting; April 1, 2013). |  | 1 | Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WALarge General ServiceThird Party ContractsPer Customer Winter Peak Reduction (kW) | WA | Large General Service | Third Party Contracts | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WALarge General ServiceThird Party ContractsPer Customer Winter Peak Reduction (%) | WA | Large General Service | Third Party Contracts | Per Customer Winter Peak Reduction (%) | % of Peak | 21% | weighted average from impacts in the following report: Impact Estimates from Aggregator Programs in California (Source: 2012 Statewide Load Impact Evaluation of California Aggregator Demand Response Programs Volume 1: Ex post and Ex ante Load Impacts; Christensen Associates Energy Consulting; April 1, 2013). |  | 1 | Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsEvent Non-Performance Rate | WA | Extra Large General Service | Third Party Contracts | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Extra Large General ServiceEvent Non-Performance Rate | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsPer Customer Summer Peak Reduction (kW) | WA | Extra Large General Service | Third Party Contracts | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsPer Customer Summer Peak Reduction (%) | WA | Extra Large General Service | Third Party Contracts | Per Customer Summer Peak Reduction (%) | % of Peak | 21% | weighted average from impacts in the following report: Impact Estimates from Aggregator Programs in California (Source: 2012 Statewide Load Impact Evaluation of California Aggregator Demand Response Programs Volume 1: Ex post and Ex ante Load Impacts; Christensen Associates Energy Consulting; April 1, 2013). |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsPer Customer Winter Peak Reduction (kW) | WA | Extra Large General Service | Third Party Contracts | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsPer Customer Winter Peak Reduction (%) | WA | Extra Large General Service | Third Party Contracts | Per Customer Winter Peak Reduction (%) | % of Peak | 21% | weighted average from impacts in the following report: Impact Estimates from Aggregator Programs in California (Source: 2012 Statewide Load Impact Evaluation of California Aggregator Demand Response Programs Volume 1: Ex post and Ex ante Load Impacts; Christensen Associates Energy Consulting; April 1, 2013). |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceAncillary Third PartyEvent Non-Performance Rate | WA | General Service | Ancillary Third Party | Event Non-Performance Rate | % |  |  |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceAncillary Third PartyPer Customer Summer Peak Reduction (kW) | WA | General Service | Ancillary Third Party | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceAncillary Third PartyPer Customer Summer Peak Reduction (%) | WA | General Service | Ancillary Third Party | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceAncillary Third PartyPer Customer Winter Peak Reduction (kW) | WA | General Service | Ancillary Third Party | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceAncillary Third PartyPer Customer Winter Peak Reduction (%) | WA | General Service | Ancillary Third Party | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WALarge General ServiceAncillary Third PartyEvent Non-Performance Rate | WA | Large General Service | Ancillary Third Party | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Large General ServiceEvent Non-Performance Rate | Market PotentialWA
WALarge General ServiceAncillary Third PartyPer Customer Summer Peak Reduction (kW) | WA | Large General Service | Ancillary Third Party | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WALarge General ServiceAncillary Third PartyPer Customer Summer Peak Reduction (%) | WA | Large General Service | Ancillary Third Party | Per Customer Summer Peak Reduction (%) | % of Peak | 15.75% | 75% of impact for ancillary |  | 1 | Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WALarge General ServiceAncillary Third PartyPer Customer Winter Peak Reduction (kW) | WA | Large General Service | Ancillary Third Party | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WALarge General ServiceAncillary Third PartyPer Customer Winter Peak Reduction (%) | WA | Large General Service | Ancillary Third Party | Per Customer Winter Peak Reduction (%) | % of Peak | 15.75% | 75% of impact for ancillary |  | 1 | Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartyEvent Non-Performance Rate | WA | Extra Large General Service | Ancillary Third Party | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Extra Large General ServiceEvent Non-Performance Rate | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartyPer Customer Summer Peak Reduction (kW) | WA | Extra Large General Service | Ancillary Third Party | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartyPer Customer Summer Peak Reduction (%) | WA | Extra Large General Service | Ancillary Third Party | Per Customer Summer Peak Reduction (%) | % of Peak | 15.75% | 75% of impact for ancillary |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartyPer Customer Winter Peak Reduction (kW) | WA | Extra Large General Service | Ancillary Third Party | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartyPer Customer Winter Peak Reduction (%) | WA | Extra Large General Service | Ancillary Third Party | Per Customer Winter Peak Reduction (%) | % of Peak | 15.75% | 75% of impact for ancillary |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceThermal Energy StorageEvent Non-Performance Rate | WA | General Service | Thermal Energy Storage | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceThermal Energy StoragePer Customer Summer Peak Reduction (kW) | WA | General Service | Thermal Energy Storage | Per Customer Summer Peak Reduction (kW) | kW @meter | 1.68 | Ice Energy - Ice Bear Tech Specifications, https://www.ice-energy.com/wp-content/uploads/2016/03/ICE-BEAR-30-Product-Sheet.pdf |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceThermal Energy StoragePer Customer Summer Peak Reduction (%) | WA | General Service | Thermal Energy Storage | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceThermal Energy StoragePer Customer Winter Peak Reduction (kW) | WA | General Service | Thermal Energy Storage | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | Removed Winter Impacts |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceThermal Energy StoragePer Customer Winter Peak Reduction (%) | WA | General Service | Thermal Energy Storage | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WALarge General ServiceThermal Energy StorageEvent Non-Performance Rate | WA | Large General Service | Thermal Energy Storage | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Large General ServiceEvent Non-Performance Rate | Market PotentialWA
WALarge General ServiceThermal Energy StoragePer Customer Summer Peak Reduction (kW) | WA | Large General Service | Thermal Energy Storage | Per Customer Summer Peak Reduction (kW) | kW @meter | 8.4 | Ice Energy - Ice Bear Tech Specifications, https://www.ice-energy.com/wp-content/uploads/2016/03/ICE-BEAR-30-Product-Sheet.pdf |  | 1 | Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WALarge General ServiceThermal Energy StoragePer Customer Summer Peak Reduction (%) | WA | Large General Service | Thermal Energy Storage | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WALarge General ServiceThermal Energy StoragePer Customer Winter Peak Reduction (kW) | WA | Large General Service | Thermal Energy Storage | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | Removed Winter Impacts |  | 1 | Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WALarge General ServiceThermal Energy StoragePer Customer Winter Peak Reduction (%) | WA | Large General Service | Thermal Energy Storage | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAExtra Large General ServiceThermal Energy StorageEvent Non-Performance Rate | WA | Extra Large General Service | Thermal Energy Storage | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Extra Large General ServiceEvent Non-Performance Rate | Market PotentialWA
WAExtra Large General ServiceThermal Energy StoragePer Customer Summer Peak Reduction (kW) | WA | Extra Large General Service | Thermal Energy Storage | Per Customer Summer Peak Reduction (kW) | kW @meter | 8.4 | Ice Energy - Ice Bear Tech Specifications, https://www.ice-energy.com/wp-content/uploads/2016/03/ICE-BEAR-30-Product-Sheet.pdf |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAExtra Large General ServiceThermal Energy StoragePer Customer Summer Peak Reduction (%) | WA | Extra Large General Service | Thermal Energy Storage | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAExtra Large General ServiceThermal Energy StoragePer Customer Winter Peak Reduction (kW) | WA | Extra Large General Service | Thermal Energy Storage | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | Removed Winter Impacts |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAExtra Large General ServiceThermal Energy StoragePer Customer Winter Peak Reduction (%) | WA | Extra Large General Service | Thermal Energy Storage | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialBattery Energy StorageEvent Non-Performance Rate | WA | Residential | Battery Energy Storage | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialBattery Energy StoragePer Customer Summer Peak Reduction (kW) | WA | Residential | Battery Energy Storage | Per Customer Summer Peak Reduction (kW) | kW @meter | 2.23 | NREL 2021: 5 kW battery * 86% round trip efficiency. Xcel Energy CO Renewable Battery Connect: 40% retention |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialBattery Energy StoragePer Customer Summer Peak Reduction (%) | WA | Residential | Battery Energy Storage | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialBattery Energy StoragePer Customer Winter Peak Reduction (kW) | WA | Residential | Battery Energy Storage | Per Customer Winter Peak Reduction (kW) | kW @meter | 2.58 | NREL 2021: 5 kW battery * 86% round trip efficiency. Xcel Energy CO Renewable Battery Connect: 40% retention |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialBattery Energy StoragePer Customer Winter Peak Reduction (%) | WA | Residential | Battery Energy Storage | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceBattery Energy StorageEvent Non-Performance Rate | WA | General Service | Battery Energy Storage | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceBattery Energy StoragePer Customer Summer Peak Reduction (kW) | WA | General Service | Battery Energy Storage | Per Customer Summer Peak Reduction (kW) | kW @meter | 2.58 | NREL 2021: 5 kW battery * 86% round trip efficiency. Xcel Energy CO Renewable Battery Connect: 40% retention |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceBattery Energy StoragePer Customer Summer Peak Reduction (%) | WA | General Service | Battery Energy Storage | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceBattery Energy StoragePer Customer Winter Peak Reduction (kW) | WA | General Service | Battery Energy Storage | Per Customer Winter Peak Reduction (kW) | kW @meter | 2.58 | NREL 2021: 5 kW battery * 86% round trip efficiency. Xcel Energy CO Renewable Battery Connect: 40% retention |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceBattery Energy StoragePer Customer Winter Peak Reduction (%) | WA | General Service | Battery Energy Storage | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WALarge General ServiceBattery Energy StorageEvent Non-Performance Rate | WA | Large General Service | Battery Energy Storage | Event Non-Performance Rate | % |  |  |  | 1 | Large General ServiceEvent Non-Performance Rate | Market PotentialWA
WALarge General ServiceBattery Energy StoragePer Customer Summer Peak Reduction (kW) | WA | Large General Service | Battery Energy Storage | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WALarge General ServiceBattery Energy StoragePer Customer Summer Peak Reduction (%) | WA | Large General Service | Battery Energy Storage | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WALarge General ServiceBattery Energy StoragePer Customer Winter Peak Reduction (kW) | WA | Large General Service | Battery Energy Storage | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WALarge General ServiceBattery Energy StoragePer Customer Winter Peak Reduction (%) | WA | Large General Service | Battery Energy Storage | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAExtra Large General ServiceBattery Energy StorageEvent Non-Performance Rate | WA | Extra Large General Service | Battery Energy Storage | Event Non-Performance Rate | % |  |  |  | 1 | Extra Large General ServiceEvent Non-Performance Rate | Market PotentialWA
WAExtra Large General ServiceBattery Energy StoragePer Customer Summer Peak Reduction (kW) | WA | Extra Large General Service | Battery Energy Storage | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAExtra Large General ServiceBattery Energy StoragePer Customer Summer Peak Reduction (%) | WA | Extra Large General Service | Battery Energy Storage | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAExtra Large General ServiceBattery Energy StoragePer Customer Winter Peak Reduction (kW) | WA | Extra Large General Service | Battery Energy Storage | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAExtra Large General ServiceBattery Energy StoragePer Customer Winter Peak Reduction (%) | WA | Extra Large General Service | Battery Energy Storage | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialAncillary Battery StorageEvent Non-Performance Rate | WA | Residential | Ancillary Battery Storage | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialAncillary Battery StoragePer Customer Summer Peak Reduction (kW) | WA | Residential | Ancillary Battery Storage | Per Customer Summer Peak Reduction (kW) | kW @meter | 2.23 | Typical battery size for segment |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialAncillary Battery StoragePer Customer Summer Peak Reduction (%) | WA | Residential | Ancillary Battery Storage | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialAncillary Battery StoragePer Customer Winter Peak Reduction (kW) | WA | Residential | Ancillary Battery Storage | Per Customer Winter Peak Reduction (kW) | kW @meter | 2.58 | Typical battery size for segment |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialAncillary Battery StoragePer Customer Winter Peak Reduction (%) | WA | Residential | Ancillary Battery Storage | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceAncillary Battery StorageEvent Non-Performance Rate | WA | General Service | Ancillary Battery Storage | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceAncillary Battery StoragePer Customer Summer Peak Reduction (kW) | WA | General Service | Ancillary Battery Storage | Per Customer Summer Peak Reduction (kW) | kW @meter | 2.58 | Typical battery size for segment |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceAncillary Battery StoragePer Customer Summer Peak Reduction (%) | WA | General Service | Ancillary Battery Storage | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceAncillary Battery StoragePer Customer Winter Peak Reduction (kW) | WA | General Service | Ancillary Battery Storage | Per Customer Winter Peak Reduction (kW) | kW @meter | 2.58 | Typical battery size for segment |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceAncillary Battery StoragePer Customer Winter Peak Reduction (%) | WA | General Service | Ancillary Battery Storage | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WALarge General ServiceAncillary Battery StorageEvent Non-Performance Rate | WA | Large General Service | Ancillary Battery Storage | Event Non-Performance Rate | % |  |  |  | 1 | Large General ServiceEvent Non-Performance Rate | Market PotentialWA
WALarge General ServiceAncillary Battery StoragePer Customer Summer Peak Reduction (kW) | WA | Large General Service | Ancillary Battery Storage | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WALarge General ServiceAncillary Battery StoragePer Customer Summer Peak Reduction (%) | WA | Large General Service | Ancillary Battery Storage | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WALarge General ServiceAncillary Battery StoragePer Customer Winter Peak Reduction (kW) | WA | Large General Service | Ancillary Battery Storage | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WALarge General ServiceAncillary Battery StoragePer Customer Winter Peak Reduction (%) | WA | Large General Service | Ancillary Battery Storage | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StorageEvent Non-Performance Rate | WA | Extra Large General Service | Ancillary Battery Storage | Event Non-Performance Rate | % |  |  |  | 1 | Extra Large General ServiceEvent Non-Performance Rate | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StoragePer Customer Summer Peak Reduction (kW) | WA | Extra Large General Service | Ancillary Battery Storage | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StoragePer Customer Summer Peak Reduction (%) | WA | Extra Large General Service | Ancillary Battery Storage | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StoragePer Customer Winter Peak Reduction (kW) | WA | Extra Large General Service | Ancillary Battery Storage | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StoragePer Customer Winter Peak Reduction (%) | WA | Extra Large General Service | Ancillary Battery Storage | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialBehavioralEvent Non-Performance Rate | WA | Residential | Behavioral | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialBehavioralPer Customer Summer Peak Reduction (kW) | WA | Residential | Behavioral | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | hi participation case = 0.75% of low to account for lower potential customers |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialBehavioralPer Customer Summer Peak Reduction (%) | WA | Residential | Behavioral | Per Customer Summer Peak Reduction (%) | % of Peak | 2% | Opower documentation for BDR with Consumers and DTE |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialBehavioralPer Customer Winter Peak Reduction (kW) | WA | Residential | Behavioral | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialBehavioralPer Customer Winter Peak Reduction (%) | WA | Residential | Behavioral | Per Customer Winter Peak Reduction (%) | % of Peak | 2% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inEvent Non-Performance Rate | WA | Residential | Pilot-Time-of-Use Opt-in | Event Non-Performance Rate | % | 0% | None - should be in eval'd number. |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inPer Customer Summer Peak Reduction (kW) | WA | Residential | Pilot-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inPer Customer Summer Peak Reduction (%) | WA | Residential | Pilot-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (%) | % of Peak | 5.7% | Brattle Analysis and Estimate - Pacificorp 2019 opt-in and opt-out scenarios |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inPer Customer Winter Peak Reduction (kW) | WA | Residential | Pilot-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inPer Customer Winter Peak Reduction (%) | WA | Residential | Pilot-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (%) | % of Peak | 2.85% | Assume 50% of Summer impacts. Brattle Analysis and Estimate - Negative impacts in Winter set to zero in Eastern states. |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inEvent Non-Performance Rate | WA | General Service | Pilot-Time-of-Use Opt-in | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inPer Customer Summer Peak Reduction (kW) | WA | General Service | Pilot-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inPer Customer Summer Peak Reduction (%) | WA | General Service | Pilot-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (%) | % of Peak | 0.2% | Brattle Analysis and Estimate - Pacificorp 2019 opt-in and opt-out scenarios |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inPer Customer Winter Peak Reduction (kW) | WA | General Service | Pilot-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inPer Customer Winter Peak Reduction (%) | WA | General Service | Pilot-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (%) | % of Peak | 0.1% | Assume 50% of Summer impacts. |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inEvent Non-Performance Rate | WA | Residential | Parent-Time-of-Use Opt-in | Event Non-Performance Rate | % | 0% | None - should be in eval'd number. |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inPer Customer Summer Peak Reduction (kW) | WA | Residential | Parent-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inPer Customer Summer Peak Reduction (%) | WA | Residential | Parent-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (%) | % of Peak | 4% | 2024 Avista Update |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inPer Customer Winter Peak Reduction (kW) | WA | Residential | Parent-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inPer Customer Winter Peak Reduction (%) | WA | Residential | Parent-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (%) | % of Peak | 1.5% | 2024 Avista Update |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inEvent Non-Performance Rate | WA | General Service | Parent-Time-of-Use Opt-in | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inPer Customer Summer Peak Reduction (kW) | WA | General Service | Parent-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inPer Customer Summer Peak Reduction (%) | WA | General Service | Parent-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (%) | % of Peak | 0.2% | Brattle Analysis and Estimate - Pacificorp 2019 opt-in and opt-out scenarios |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inPer Customer Winter Peak Reduction (kW) | WA | General Service | Parent-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inPer Customer Winter Peak Reduction (%) | WA | General Service | Parent-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (%) | % of Peak | 0.1% | Assume 50% of Summer impacts. |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inEvent Non-Performance Rate | WA | Large General Service | Parent-Time-of-Use Opt-in | Event Non-Performance Rate | % |  |  |  | 1 | Large General ServiceEvent Non-Performance Rate | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inPer Customer Summer Peak Reduction (kW) | WA | Large General Service | Parent-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inPer Customer Summer Peak Reduction (%) | WA | Large General Service | Parent-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inPer Customer Winter Peak Reduction (kW) | WA | Large General Service | Parent-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inPer Customer Winter Peak Reduction (%) | WA | Large General Service | Parent-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inEvent Non-Performance Rate | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Event Non-Performance Rate | % |  |  |  | 1 | Extra Large General ServiceEvent Non-Performance Rate | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inPer Customer Summer Peak Reduction (kW) | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inPer Customer Summer Peak Reduction (%) | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inPer Customer Winter Peak Reduction (kW) | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inPer Customer Winter Peak Reduction (%) | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialTime-of-Use Opt-OutEvent Non-Performance Rate | WA | Residential | Time-of-Use Opt-Out | Event Non-Performance Rate | % | 0% | None - should be in eval'd number. |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialTime-of-Use Opt-OutPer Customer Summer Peak Reduction (kW) | WA | Residential | Time-of-Use Opt-Out | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialTime-of-Use Opt-OutPer Customer Summer Peak Reduction (%) | WA | Residential | Time-of-Use Opt-Out | Per Customer Summer Peak Reduction (%) | % of Peak | 1.5% | 2024 Avista Update |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialTime-of-Use Opt-OutPer Customer Winter Peak Reduction (kW) | WA | Residential | Time-of-Use Opt-Out | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialTime-of-Use Opt-OutPer Customer Winter Peak Reduction (%) | WA | Residential | Time-of-Use Opt-Out | Per Customer Winter Peak Reduction (%) | % of Peak | 0.2% | 2024 Avista Update |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutEvent Non-Performance Rate | WA | General Service | Time-of-Use Opt-Out | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutPer Customer Summer Peak Reduction (kW) | WA | General Service | Time-of-Use Opt-Out | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutPer Customer Summer Peak Reduction (%) | WA | General Service | Time-of-Use Opt-Out | Per Customer Summer Peak Reduction (%) | % of Peak | 0.2% | Brattle Analysis and Estimate - Pacificorp 2019 opt-in and opt-out scenarios |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutPer Customer Winter Peak Reduction (kW) | WA | General Service | Time-of-Use Opt-Out | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutPer Customer Winter Peak Reduction (%) | WA | General Service | Time-of-Use Opt-Out | Per Customer Winter Peak Reduction (%) | % of Peak | 0.1% | Assume 50% of Summer impacts. |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutEvent Non-Performance Rate | WA | Large General Service | Time-of-Use Opt-Out | Event Non-Performance Rate | % |  |  |  | 1 | Large General ServiceEvent Non-Performance Rate | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutPer Customer Summer Peak Reduction (kW) | WA | Large General Service | Time-of-Use Opt-Out | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutPer Customer Summer Peak Reduction (%) | WA | Large General Service | Time-of-Use Opt-Out | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutPer Customer Winter Peak Reduction (kW) | WA | Large General Service | Time-of-Use Opt-Out | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutPer Customer Winter Peak Reduction (%) | WA | Large General Service | Time-of-Use Opt-Out | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutEvent Non-Performance Rate | WA | Extra Large General Service | Time-of-Use Opt-Out | Event Non-Performance Rate | % |  |  |  | 1 | Extra Large General ServiceEvent Non-Performance Rate | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutPer Customer Summer Peak Reduction (kW) | WA | Extra Large General Service | Time-of-Use Opt-Out | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutPer Customer Summer Peak Reduction (%) | WA | Extra Large General Service | Time-of-Use Opt-Out | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutPer Customer Winter Peak Reduction (kW) | WA | Extra Large General Service | Time-of-Use Opt-Out | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutPer Customer Winter Peak Reduction (%) | WA | Extra Large General Service | Time-of-Use Opt-Out | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inEvent Non-Performance Rate | WA | GS-EV | Electric Vehicle TOU Opt-in | Event Non-Performance Rate | % | 0% | 0 |  | 1 | GS-EVEvent Non-Performance Rate | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inPer Customer Summer Peak Reduction (kW) | WA | GS-EV | Electric Vehicle TOU Opt-in | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | GS-EVPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inPer Customer Summer Peak Reduction (%) | WA | GS-EV | Electric Vehicle TOU Opt-in | Per Customer Summer Peak Reduction (%) | % of Peak | 100% | 2024 Avista Update: of total EV load instead of total HH load |  | 1 | GS-EVPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inPer Customer Winter Peak Reduction (kW) | WA | GS-EV | Electric Vehicle TOU Opt-in | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | GS-EVPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inPer Customer Winter Peak Reduction (%) | WA | GS-EV | Electric Vehicle TOU Opt-in | Per Customer Winter Peak Reduction (%) | % of Peak | 100% | 2024 Avista Update: of total EV load instead of total HH load |  | 1 | GS-EVPer Customer Winter Peak Reduction (%) | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inEvent Non-Performance Rate | WA | LGS-EV | Electric Vehicle TOU Opt-in | Event Non-Performance Rate | % | 0% | 0 |  | 1 | LGS-EVEvent Non-Performance Rate | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inPer Customer Summer Peak Reduction (kW) | WA | LGS-EV | Electric Vehicle TOU Opt-in | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | LGS-EVPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inPer Customer Summer Peak Reduction (%) | WA | LGS-EV | Electric Vehicle TOU Opt-in | Per Customer Summer Peak Reduction (%) | % of Peak | 100% | 2024 Avista Update: of total EV load instead of total HH load |  | 1 | LGS-EVPer Customer Summer Peak Reduction (%) | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inPer Customer Winter Peak Reduction (kW) | WA | LGS-EV | Electric Vehicle TOU Opt-in | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | LGS-EVPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inPer Customer Winter Peak Reduction (%) | WA | LGS-EV | Electric Vehicle TOU Opt-in | Per Customer Winter Peak Reduction (%) | % of Peak | 100% | 2024 Avista Update: of total EV load instead of total HH load |  | 1 | LGS-EVPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialPilot-Peak Time RebateEvent Non-Performance Rate | WA | Residential | Pilot-Peak Time Rebate | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialPilot-Peak Time RebatePer Customer Summer Peak Reduction (kW) | WA | Residential | Pilot-Peak Time Rebate | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialPilot-Peak Time RebatePer Customer Summer Peak Reduction (%) | WA | Residential | Pilot-Peak Time Rebate | Per Customer Summer Peak Reduction (%) | % of Peak | 8.2% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: 0.159 or 8.2% in summer, 0.134 or 7.1% in winter |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialPilot-Peak Time RebatePer Customer Winter Peak Reduction (kW) | WA | Residential | Pilot-Peak Time Rebate | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialPilot-Peak Time RebatePer Customer Winter Peak Reduction (%) | WA | Residential | Pilot-Peak Time Rebate | Per Customer Winter Peak Reduction (%) | % of Peak | 7.1% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: 0.159 or 8.2% in summer, 0.134 or 7.1% in winter |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebateEvent Non-Performance Rate | WA | General Service | Pilot-Peak Time Rebate | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebatePer Customer Summer Peak Reduction (kW) | WA | General Service | Pilot-Peak Time Rebate | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebatePer Customer Summer Peak Reduction (%) | WA | General Service | Pilot-Peak Time Rebate | Per Customer Summer Peak Reduction (%) | % of Peak | 4.1% | Assumes half residential estimates from PGE Flex 2.0 PTR pilot evaliation 2021 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebatePer Customer Winter Peak Reduction (kW) | WA | General Service | Pilot-Peak Time Rebate | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebatePer Customer Winter Peak Reduction (%) | WA | General Service | Pilot-Peak Time Rebate | Per Customer Winter Peak Reduction (%) | % of Peak | 3.55% | Assumes half residential estimates from PGE Flex 2.0 PTR pilot evaliation 2021 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAResidentialParent-Peak Time RebateEvent Non-Performance Rate | WA | Residential | Parent-Peak Time Rebate | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialWA
WAResidentialParent-Peak Time RebatePer Customer Summer Peak Reduction (kW) | WA | Residential | Parent-Peak Time Rebate | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAResidentialParent-Peak Time RebatePer Customer Summer Peak Reduction (%) | WA | Residential | Parent-Peak Time Rebate | Per Customer Summer Peak Reduction (%) | % of Peak | 8.2% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: 0.159 or 8.2% in summer, 0.134 or 7.1% in winter |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialWA
WAResidentialParent-Peak Time RebatePer Customer Winter Peak Reduction (kW) | WA | Residential | Parent-Peak Time Rebate | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAResidentialParent-Peak Time RebatePer Customer Winter Peak Reduction (%) | WA | Residential | Parent-Peak Time Rebate | Per Customer Winter Peak Reduction (%) | % of Peak | 7.1% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: 0.159 or 8.2% in summer, 0.134 or 7.1% in winter |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebateEvent Non-Performance Rate | WA | General Service | Parent-Peak Time Rebate | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebatePer Customer Summer Peak Reduction (kW) | WA | General Service | Parent-Peak Time Rebate | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebatePer Customer Summer Peak Reduction (%) | WA | General Service | Parent-Peak Time Rebate | Per Customer Summer Peak Reduction (%) | % of Peak | 4.1% | Assumes half residential estimates from PGE Flex 2.0 PTR pilot evaliation 2021 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebatePer Customer Winter Peak Reduction (kW) | WA | General Service | Parent-Peak Time Rebate | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebatePer Customer Winter Peak Reduction (%) | WA | General Service | Parent-Peak Time Rebate | Per Customer Winter Peak Reduction (%) | % of Peak | 3.55% | Assumes half residential estimates from PGE Flex 2.0 PTR pilot evaliation 2021 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesEvent Non-Performance Rate | WA | Large General Service | Variable Peak Pricing Rates | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Large General ServiceEvent Non-Performance Rate | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesPer Customer Summer Peak Reduction (kW) | WA | Large General Service | Variable Peak Pricing Rates | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesPer Customer Summer Peak Reduction (%) | WA | Large General Service | Variable Peak Pricing Rates | Per Customer Summer Peak Reduction (%) | % of Peak | 4% | OG&E 2017 Smart Hours Study - 4% for an average CPE day for VPP only customers without a smart thermostat |  | 1 | Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesPer Customer Winter Peak Reduction (kW) | WA | Large General Service | Variable Peak Pricing Rates | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesPer Customer Winter Peak Reduction (%) | WA | Large General Service | Variable Peak Pricing Rates | Per Customer Winter Peak Reduction (%) | % of Peak | 3% | 0 |  | 1 | Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesEvent Non-Performance Rate | WA | Extra Large General Service | Variable Peak Pricing Rates | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Extra Large General ServiceEvent Non-Performance Rate | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesPer Customer Summer Peak Reduction (kW) | WA | Extra Large General Service | Variable Peak Pricing Rates | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesPer Customer Summer Peak Reduction (%) | WA | Extra Large General Service | Variable Peak Pricing Rates | Per Customer Summer Peak Reduction (%) | % of Peak | 4% | OG&E 2017 Smart Hours Study - 4% for an average CPE day for VPP only customers without a smart thermostat |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesPer Customer Winter Peak Reduction (kW) | WA | Extra Large General Service | Variable Peak Pricing Rates | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesPer Customer Winter Peak Reduction (%) | WA | Extra Large General Service | Variable Peak Pricing Rates | Per Customer Winter Peak Reduction (%) | % of Peak | 3% | 0 |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialWA
IDResidentialDLC Central ACEvent Non-Performance Rate | ID | Residential | DLC Central AC | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialDLC Central ACPer Customer Summer Peak Reduction (kW) | ID | Residential | DLC Central AC | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.5 | NWPC DLC Switch cooling assumption (east) |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialDLC Central ACPer Customer Summer Peak Reduction (%) | ID | Residential | DLC Central AC | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialDLC Central ACPer Customer Winter Peak Reduction (kW) | ID | Residential | DLC Central AC | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialDLC Central ACPer Customer Winter Peak Reduction (%) | ID | Residential | DLC Central AC | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceDLC Central ACEvent Non-Performance Rate | ID | General Service | DLC Central AC | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceDLC Central ACPer Customer Summer Peak Reduction (kW) | ID | General Service | DLC Central AC | Per Customer Summer Peak Reduction (kW) | kW @meter | 1.25 | NWPC DLC Switch cooling assumption (East) |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceDLC Central ACPer Customer Summer Peak Reduction (%) | ID | General Service | DLC Central AC | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceDLC Central ACPer Customer Winter Peak Reduction (kW) | ID | General Service | DLC Central AC | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceDLC Central ACPer Customer Winter Peak Reduction (%) | ID | General Service | DLC Central AC | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingEvent Non-Performance Rate | ID | Residential | DLC Smart Thermostats - Cooling | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingPer Customer Summer Peak Reduction (kW) | ID | Residential | DLC Smart Thermostats - Cooling | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.5 | NWPC DLC Switch cooling assumption (east)- Thermostat impact was 1.27 kW but didn't seem right so we defaulted to DLC Central AC |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingPer Customer Summer Peak Reduction (%) | ID | Residential | DLC Smart Thermostats - Cooling | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingPer Customer Winter Peak Reduction (kW) | ID | Residential | DLC Smart Thermostats - Cooling | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingPer Customer Winter Peak Reduction (%) | ID | Residential | DLC Smart Thermostats - Cooling | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingEvent Non-Performance Rate | ID | General Service | DLC Smart Thermostats - Cooling | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingPer Customer Summer Peak Reduction (kW) | ID | General Service | DLC Smart Thermostats - Cooling | Per Customer Summer Peak Reduction (kW) | kW @meter | 1.25 | NWPC DLC Switch cooling assumption (East) |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingPer Customer Summer Peak Reduction (%) | ID | General Service | DLC Smart Thermostats - Cooling | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingPer Customer Winter Peak Reduction (kW) | ID | General Service | DLC Smart Thermostats - Cooling | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingPer Customer Winter Peak Reduction (%) | ID | General Service | DLC Smart Thermostats - Cooling | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialAncillary CoolingEvent Non-Performance Rate | ID | Residential | Ancillary Cooling | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialAncillary CoolingPer Customer Summer Peak Reduction (kW) | ID | Residential | Ancillary Cooling | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.25 | Half of parent thermostat impact for ancillary |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialAncillary CoolingPer Customer Summer Peak Reduction (%) | ID | Residential | Ancillary Cooling | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialAncillary CoolingPer Customer Winter Peak Reduction (kW) | ID | Residential | Ancillary Cooling | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialAncillary CoolingPer Customer Winter Peak Reduction (%) | ID | Residential | Ancillary Cooling | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceAncillary CoolingEvent Non-Performance Rate | ID | General Service | Ancillary Cooling | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceAncillary CoolingPer Customer Summer Peak Reduction (kW) | ID | General Service | Ancillary Cooling | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.625 | NWPC DLC Switch cooling assumption (East)- Half impact for ancillary |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceAncillary CoolingPer Customer Summer Peak Reduction (%) | ID | General Service | Ancillary Cooling | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceAncillary CoolingPer Customer Winter Peak Reduction (kW) | ID | General Service | Ancillary Cooling | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceAncillary CoolingPer Customer Winter Peak Reduction (%) | ID | General Service | Ancillary Cooling | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingEvent Non-Performance Rate | ID | Residential | DLC Smart Thermostats - Heating | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingPer Customer Summer Peak Reduction (kW) | ID | Residential | DLC Smart Thermostats - Heating | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingPer Customer Summer Peak Reduction (%) | ID | Residential | DLC Smart Thermostats - Heating | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingPer Customer Winter Peak Reduction (kW) | ID | Residential | DLC Smart Thermostats - Heating | Per Customer Winter Peak Reduction (kW) | kW @meter | 1.09 | NWPC Smart thermostat heating assumption- general service uses 0.54 (switch to thermostat impact ratio) of eastern switch impact |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingPer Customer Winter Peak Reduction (%) | ID | Residential | DLC Smart Thermostats - Heating | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingEvent Non-Performance Rate | ID | General Service | DLC Smart Thermostats - Heating | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingPer Customer Summer Peak Reduction (kW) | ID | General Service | DLC Smart Thermostats - Heating | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingPer Customer Summer Peak Reduction (%) | ID | General Service | DLC Smart Thermostats - Heating | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingPer Customer Winter Peak Reduction (kW) | ID | General Service | DLC Smart Thermostats - Heating | Per Customer Winter Peak Reduction (kW) | kW @meter | 1.35 | NWPC Smart thermostat heating assumption- general service uses 0.54 (switch to thermostat impact ratio) of eastern switch impact of 2.5 |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingPer Customer Winter Peak Reduction (%) | ID | General Service | DLC Smart Thermostats - Heating | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialAncillary HeatingEvent Non-Performance Rate | ID | Residential | Ancillary Heating | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialAncillary HeatingPer Customer Summer Peak Reduction (kW) | ID | Residential | Ancillary Heating | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialAncillary HeatingPer Customer Summer Peak Reduction (%) | ID | Residential | Ancillary Heating | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialAncillary HeatingPer Customer Winter Peak Reduction (kW) | ID | Residential | Ancillary Heating | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.545 | Half of Smart Thermostat Heating Per-Customer Impact |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialAncillary HeatingPer Customer Winter Peak Reduction (%) | ID | Residential | Ancillary Heating | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceAncillary HeatingEvent Non-Performance Rate | ID | General Service | Ancillary Heating | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceAncillary HeatingPer Customer Summer Peak Reduction (kW) | ID | General Service | Ancillary Heating | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceAncillary HeatingPer Customer Summer Peak Reduction (%) | ID | General Service | Ancillary Heating | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceAncillary HeatingPer Customer Winter Peak Reduction (kW) | ID | General Service | Ancillary Heating | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.675 | Half of parent Smart Thermostat-Heating per-customer impacts |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceAncillary HeatingPer Customer Winter Peak Reduction (%) | ID | General Service | Ancillary Heating | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialDLC Water HeatingEvent Non-Performance Rate | ID | Residential | DLC Water Heating | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialDLC Water HeatingPer Customer Summer Peak Reduction (kW) | ID | Residential | DLC Water Heating | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.2 | NWPC Electric Resistance Switch Summer Impact, derated to align with Wh proportion of peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialDLC Water HeatingPer Customer Summer Peak Reduction (%) | ID | Residential | DLC Water Heating | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialDLC Water HeatingPer Customer Winter Peak Reduction (kW) | ID | Residential | DLC Water Heating | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.2 | NWPC Electric Resistance Switch Winter Impact, derated to align with Wh proportion of peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialDLC Water HeatingPer Customer Winter Peak Reduction (%) | ID | Residential | DLC Water Heating | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceDLC Water HeatingEvent Non-Performance Rate | ID | General Service | DLC Water Heating | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceDLC Water HeatingPer Customer Summer Peak Reduction (kW) | ID | General Service | DLC Water Heating | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.504 | 7th Plan, pg 25 from Cadmnus Report, Commercial: Res value multiplied by the CAC DLC ratio (small C&I impact /Res impact) |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceDLC Water HeatingPer Customer Summer Peak Reduction (%) | ID | General Service | DLC Water Heating | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceDLC Water HeatingPer Customer Winter Peak Reduction (kW) | ID | General Service | DLC Water Heating | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.504 | 7th Plan, pg 25 from Cadmnus Report, Commercial: Res value multiplied by the CAC DLC ratio (small C&I impact /Res impact) |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceDLC Water HeatingPer Customer Winter Peak Reduction (%) | ID | General Service | DLC Water Heating | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialAncillary DLC WHEvent Non-Performance Rate | ID | Residential | Ancillary DLC WH | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialAncillary DLC WHPer Customer Summer Peak Reduction (kW) | ID | Residential | Ancillary DLC WH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.2 | NWPC Electric Resistance Switch Summer Impact, derated to align with Wh proportion of peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialAncillary DLC WHPer Customer Summer Peak Reduction (%) | ID | Residential | Ancillary DLC WH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialAncillary DLC WHPer Customer Winter Peak Reduction (kW) | ID | Residential | Ancillary DLC WH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.2 | NWPC Electric Resistance Switch Winter Impact, derated to align with Wh proportion of peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialAncillary DLC WHPer Customer Winter Peak Reduction (%) | ID | Residential | Ancillary DLC WH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceAncillary DLC WHEvent Non-Performance Rate | ID | General Service | Ancillary DLC WH | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceAncillary DLC WHPer Customer Summer Peak Reduction (kW) | ID | General Service | Ancillary DLC WH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.504 | 7th Plan, pg 25 from Cadmnus Report, Commercial: Res value multiplied by the CAC DLC ratio (small C&I impact /Res impact) |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceAncillary DLC WHPer Customer Summer Peak Reduction (%) | ID | General Service | Ancillary DLC WH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceAncillary DLC WHPer Customer Winter Peak Reduction (kW) | ID | General Service | Ancillary DLC WH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.504 | 7th Plan, pg 25 from Cadmnus Report, Commercial: Res value multiplied by the CAC DLC ratio (small C&I impact /Res impact) |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceAncillary DLC WHPer Customer Winter Peak Reduction (%) | ID | General Service | Ancillary DLC WH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHEvent Non-Performance Rate | ID | Residential | Pilot-CTA-2045 HPWH | Event Non-Performance Rate | % | 0% | Ability for customers to easily override event- using 3% as placeholder |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHPer Customer Summer Peak Reduction (kW) | ID | Residential | Pilot-CTA-2045 HPWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHPer Customer Summer Peak Reduction (%) | ID | Residential | Pilot-CTA-2045 HPWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHPer Customer Winter Peak Reduction (kW) | ID | Residential | Pilot-CTA-2045 HPWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHPer Customer Winter Peak Reduction (%) | ID | Residential | Pilot-CTA-2045 HPWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHEvent Non-Performance Rate | ID | General Service | Pilot-CTA-2045 HPWH | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHPer Customer Summer Peak Reduction (kW) | ID | General Service | Pilot-CTA-2045 HPWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHPer Customer Summer Peak Reduction (%) | ID | General Service | Pilot-CTA-2045 HPWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHPer Customer Winter Peak Reduction (kW) | ID | General Service | Pilot-CTA-2045 HPWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHPer Customer Winter Peak Reduction (%) | ID | General Service | Pilot-CTA-2045 HPWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialParent-CTA-2045 HPWHEvent Non-Performance Rate | ID | Residential | Parent-CTA-2045 HPWH | Event Non-Performance Rate | % | 0% | Ability for customers to easily override event- using 3% as placeholder |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialParent-CTA-2045 HPWHPer Customer Summer Peak Reduction (kW) | ID | Residential | Parent-CTA-2045 HPWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialParent-CTA-2045 HPWHPer Customer Summer Peak Reduction (%) | ID | Residential | Parent-CTA-2045 HPWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialParent-CTA-2045 HPWHPer Customer Winter Peak Reduction (kW) | ID | Residential | Parent-CTA-2045 HPWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialParent-CTA-2045 HPWHPer Customer Winter Peak Reduction (%) | ID | Residential | Parent-CTA-2045 HPWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHEvent Non-Performance Rate | ID | General Service | Parent-CTA-2045 HPWH | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHPer Customer Summer Peak Reduction (kW) | ID | General Service | Parent-CTA-2045 HPWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHPer Customer Summer Peak Reduction (%) | ID | General Service | Parent-CTA-2045 HPWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHPer Customer Winter Peak Reduction (kW) | ID | General Service | Parent-CTA-2045 HPWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.56x of res |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHPer Customer Winter Peak Reduction (%) | ID | General Service | Parent-CTA-2045 HPWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialPilot-Ancillary HPWHEvent Non-Performance Rate | ID | Residential | Pilot-Ancillary HPWH | Event Non-Performance Rate | % | 0% | Ability for customers to easily override event- using 3% as placeholder |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialPilot-Ancillary HPWHPer Customer Summer Peak Reduction (kW) | ID | Residential | Pilot-Ancillary HPWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialPilot-Ancillary HPWHPer Customer Summer Peak Reduction (%) | ID | Residential | Pilot-Ancillary HPWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialPilot-Ancillary HPWHPer Customer Winter Peak Reduction (kW) | ID | Residential | Pilot-Ancillary HPWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialPilot-Ancillary HPWHPer Customer Winter Peak Reduction (%) | ID | Residential | Pilot-Ancillary HPWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHEvent Non-Performance Rate | ID | General Service | Pilot-Ancillary HPWH | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHPer Customer Summer Peak Reduction (kW) | ID | General Service | Pilot-Ancillary HPWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHPer Customer Summer Peak Reduction (%) | ID | General Service | Pilot-Ancillary HPWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHPer Customer Winter Peak Reduction (kW) | ID | General Service | Pilot-Ancillary HPWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHPer Customer Winter Peak Reduction (%) | ID | General Service | Pilot-Ancillary HPWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialParent-Ancillary HPWHEvent Non-Performance Rate | ID | Residential | Parent-Ancillary HPWH | Event Non-Performance Rate | % | 0% | Ability for customers to easily override event- using 3% as placeholder |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialParent-Ancillary HPWHPer Customer Summer Peak Reduction (kW) | ID | Residential | Parent-Ancillary HPWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialParent-Ancillary HPWHPer Customer Summer Peak Reduction (%) | ID | Residential | Parent-Ancillary HPWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialParent-Ancillary HPWHPer Customer Winter Peak Reduction (kW) | ID | Residential | Parent-Ancillary HPWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialParent-Ancillary HPWHPer Customer Winter Peak Reduction (%) | ID | Residential | Parent-Ancillary HPWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHEvent Non-Performance Rate | ID | General Service | Parent-Ancillary HPWH | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHPer Customer Summer Peak Reduction (kW) | ID | General Service | Parent-Ancillary HPWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHPer Customer Summer Peak Reduction (%) | ID | General Service | Parent-Ancillary HPWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHPer Customer Winter Peak Reduction (kW) | ID | General Service | Parent-Ancillary HPWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHPer Customer Winter Peak Reduction (%) | ID | General Service | Parent-Ancillary HPWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHEvent Non-Performance Rate | ID | Residential | Pilot-CTA-2045 ERWH | Event Non-Performance Rate | % | 0% | Ability for customers to easily override event- using 3% as placeholder |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHPer Customer Summer Peak Reduction (kW) | ID | Residential | Pilot-CTA-2045 ERWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH proportion of peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHPer Customer Summer Peak Reduction (%) | ID | Residential | Pilot-CTA-2045 ERWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHPer Customer Winter Peak Reduction (kW) | ID | Residential | Pilot-CTA-2045 ERWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Winter AM impact, derated to align with WH proportion of peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHPer Customer Winter Peak Reduction (%) | ID | Residential | Pilot-CTA-2045 ERWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHEvent Non-Performance Rate | ID | General Service | Pilot-CTA-2045 ERWH | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHPer Customer Summer Peak Reduction (kW) | ID | General Service | Pilot-CTA-2045 ERWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHPer Customer Summer Peak Reduction (%) | ID | General Service | Pilot-CTA-2045 ERWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHPer Customer Winter Peak Reduction (kW) | ID | General Service | Pilot-CTA-2045 ERWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHPer Customer Winter Peak Reduction (%) | ID | General Service | Pilot-CTA-2045 ERWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialParent-CTA-2045 ERWHEvent Non-Performance Rate | ID | Residential | Parent-CTA-2045 ERWH | Event Non-Performance Rate | % | 0% | Ability for customers to easily override event- using 3% as placeholder |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialParent-CTA-2045 ERWHPer Customer Summer Peak Reduction (kW) | ID | Residential | Parent-CTA-2045 ERWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH proportion of peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialParent-CTA-2045 ERWHPer Customer Summer Peak Reduction (%) | ID | Residential | Parent-CTA-2045 ERWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialParent-CTA-2045 ERWHPer Customer Winter Peak Reduction (kW) | ID | Residential | Parent-CTA-2045 ERWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Winter AM impact, derated to align with WH proportion of peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialParent-CTA-2045 ERWHPer Customer Winter Peak Reduction (%) | ID | Residential | Parent-CTA-2045 ERWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHEvent Non-Performance Rate | ID | General Service | Parent-CTA-2045 ERWH | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHPer Customer Summer Peak Reduction (kW) | ID | General Service | Parent-CTA-2045 ERWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHPer Customer Summer Peak Reduction (%) | ID | General Service | Parent-CTA-2045 ERWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHPer Customer Winter Peak Reduction (kW) | ID | General Service | Parent-CTA-2045 ERWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHPer Customer Winter Peak Reduction (%) | ID | General Service | Parent-CTA-2045 ERWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialPilot-Ancillary ERWHEvent Non-Performance Rate | ID | Residential | Pilot-Ancillary ERWH | Event Non-Performance Rate | % | 0% | Ability for customers to easily override event- using 3% as placeholder |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialPilot-Ancillary ERWHPer Customer Summer Peak Reduction (kW) | ID | Residential | Pilot-Ancillary ERWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH proportion of peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialPilot-Ancillary ERWHPer Customer Summer Peak Reduction (%) | ID | Residential | Pilot-Ancillary ERWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialPilot-Ancillary ERWHPer Customer Winter Peak Reduction (kW) | ID | Residential | Pilot-Ancillary ERWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Winter AM impact, derated to align with WH proportion of peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialPilot-Ancillary ERWHPer Customer Winter Peak Reduction (%) | ID | Residential | Pilot-Ancillary ERWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHEvent Non-Performance Rate | ID | General Service | Pilot-Ancillary ERWH | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHPer Customer Summer Peak Reduction (kW) | ID | General Service | Pilot-Ancillary ERWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHPer Customer Summer Peak Reduction (%) | ID | General Service | Pilot-Ancillary ERWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHPer Customer Winter Peak Reduction (kW) | ID | General Service | Pilot-Ancillary ERWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHPer Customer Winter Peak Reduction (%) | ID | General Service | Pilot-Ancillary ERWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialParent-Ancillary ERWHEvent Non-Performance Rate | ID | Residential | Parent-Ancillary ERWH | Event Non-Performance Rate | % | 0% | Ability for customers to easily override event- using 3% as placeholder |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialParent-Ancillary ERWHPer Customer Summer Peak Reduction (kW) | ID | Residential | Parent-Ancillary ERWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH proportion of peak load from EE study |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialParent-Ancillary ERWHPer Customer Summer Peak Reduction (%) | ID | Residential | Parent-Ancillary ERWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialParent-Ancillary ERWHPer Customer Winter Peak Reduction (kW) | ID | Residential | Parent-Ancillary ERWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | BPA 2018 CTA-2045 Water Heater Demonstration Report- Winter AM impact, derated to align with WH proportion of peak load from EE study |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialParent-Ancillary ERWHPer Customer Winter Peak Reduction (%) | ID | Residential | Parent-Ancillary ERWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHEvent Non-Performance Rate | ID | General Service | Parent-Ancillary ERWH | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHPer Customer Summer Peak Reduction (kW) | ID | General Service | Parent-Ancillary ERWH | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHPer Customer Summer Peak Reduction (%) | ID | General Service | Parent-Ancillary ERWH | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHPer Customer Winter Peak Reduction (kW) | ID | General Service | Parent-Ancillary ERWH | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHPer Customer Winter Peak Reduction (%) | ID | General Service | Parent-Ancillary ERWH | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialDLC Smart AppliancesEvent Non-Performance Rate | ID | Residential | DLC Smart Appliances | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialDLC Smart AppliancesPer Customer Summer Peak Reduction (kW) | ID | Residential | DLC Smart Appliances | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.14 | Ghatikar, Rish. Demand Response Automation in Appliance and Equipment. Lawrence Berkley National Laboratory, 2015. Web. http://docketpublic.energy.ca.gov/PublicDocuments/15-IEPR-05/TN205072_20150618T110004_Demand_Response_Automation_in_Appliances_and_Equipment.pptx kw @ meter values= 0.14 for summer and winter |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialDLC Smart AppliancesPer Customer Summer Peak Reduction (%) | ID | Residential | DLC Smart Appliances | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialDLC Smart AppliancesPer Customer Winter Peak Reduction (kW) | ID | Residential | DLC Smart Appliances | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.14 | Ghatikar, Rish. Demand Response Automation in Appliance and Equipment. Lawrence Berkley National Laboratory, 2015. Web. http://docketpublic.energy.ca.gov/PublicDocuments/15-IEPR-05/TN205072_20150618T110004_Demand_Response_Automation_in_Appliances_and_Equipment.pptx kw @ meter values= 0.14 for summer and winter |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialDLC Smart AppliancesPer Customer Winter Peak Reduction (%) | ID | Residential | DLC Smart Appliances | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesEvent Non-Performance Rate | ID | General Service | DLC Smart Appliances | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesPer Customer Summer Peak Reduction (kW) | ID | General Service | DLC Smart Appliances | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.14 | Ghatikar, Rish. Demand Response Automation in Appliance and Equipment. Lawrence Berkley National Laboratory, 2015. Web. http://docketpublic.energy.ca.gov/PublicDocuments/15-IEPR-05/TN205072_20150618T110004_Demand_Response_Automation_in_Appliances_and_Equipment.pptx kw @ meter values= 0.14 for summer and winter |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesPer Customer Summer Peak Reduction (%) | ID | General Service | DLC Smart Appliances | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesPer Customer Winter Peak Reduction (kW) | ID | General Service | DLC Smart Appliances | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.14 | Ghatikar, Rish. Demand Response Automation in Appliance and Equipment. Lawrence Berkley National Laboratory, 2015. Web. http://docketpublic.energy.ca.gov/PublicDocuments/15-IEPR-05/TN205072_20150618T110004_Demand_Response_Automation_in_Appliances_and_Equipment.pptx kw @ meter values= 0.14 for summer and winter |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesPer Customer Winter Peak Reduction (%) | ID | General Service | DLC Smart Appliances | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingEvent Non-Performance Rate | ID | Res-EV | DLC Electric Vehicle Charging | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Res-EVEvent Non-Performance Rate | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingPer Customer Summer Peak Reduction (kW) | ID | Res-EV | DLC Electric Vehicle Charging | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | Update: Avista 2019 EVSE report claims 75% charging load reduction. Impact based on Res-EV impact/customer. OLD: Based on Avista research, expecting a 90% + Load Shift (0.5 kW) |  | 1 | Res-EVPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingPer Customer Summer Peak Reduction (%) | ID | Res-EV | DLC Electric Vehicle Charging | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 2024 Avista Update |  | 1 | Res-EVPer Customer Summer Peak Reduction (%) | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingPer Customer Winter Peak Reduction (kW) | ID | Res-EV | DLC Electric Vehicle Charging | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | Update: Avista 2019 EVSE report claims 75% charging load reduction. Impact based on Res-EV impact/customer. OLD: Based on Avista research, expecting a 90% + Load Shift (0.5 kW) |  | 1 | Res-EVPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingPer Customer Winter Peak Reduction (%) | ID | Res-EV | DLC Electric Vehicle Charging | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 2024 Avista Update |  | 1 | Res-EVPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingEvent Non-Performance Rate | ID | GS-EV | DLC Electric Vehicle Charging | Event Non-Performance Rate | % |  |  |  | 1 | GS-EVEvent Non-Performance Rate | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingPer Customer Summer Peak Reduction (kW) | ID | GS-EV | DLC Electric Vehicle Charging | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | GS-EVPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingPer Customer Summer Peak Reduction (%) | ID | GS-EV | DLC Electric Vehicle Charging | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | GS-EVPer Customer Summer Peak Reduction (%) | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingPer Customer Winter Peak Reduction (kW) | ID | GS-EV | DLC Electric Vehicle Charging | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | GS-EVPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingPer Customer Winter Peak Reduction (%) | ID | GS-EV | DLC Electric Vehicle Charging | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | GS-EVPer Customer Winter Peak Reduction (%) | Market PotentialID
IDRes-EVAncillary EVEvent Non-Performance Rate | ID | Res-EV | Ancillary EV | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Res-EVEvent Non-Performance Rate | Market PotentialID
IDRes-EVAncillary EVPer Customer Summer Peak Reduction (kW) | ID | Res-EV | Ancillary EV | Per Customer Summer Peak Reduction (kW) | kW @meter | 0.25 | Half of parent impact for ancillary |  | 1 | Res-EVPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDRes-EVAncillary EVPer Customer Summer Peak Reduction (%) | ID | Res-EV | Ancillary EV | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | Res-EVPer Customer Summer Peak Reduction (%) | Market PotentialID
IDRes-EVAncillary EVPer Customer Winter Peak Reduction (kW) | ID | Res-EV | Ancillary EV | Per Customer Winter Peak Reduction (kW) | kW @meter | 0.25 | Half of parent impact for ancillary |  | 1 | Res-EVPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDRes-EVAncillary EVPer Customer Winter Peak Reduction (%) | ID | Res-EV | Ancillary EV | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | Res-EVPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGS-EVAncillary EVEvent Non-Performance Rate | ID | GS-EV | Ancillary EV | Event Non-Performance Rate | % | 0% | 0 |  | 1 | GS-EVEvent Non-Performance Rate | Market PotentialID
IDGS-EVAncillary EVPer Customer Summer Peak Reduction (kW) | ID | GS-EV | Ancillary EV | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | Update: Avista 2019 EVSE report claims 75% charging load reduction. Impact based on Res-EV impact/customer. OLD: Based on Avista research, expecting a 90% + Load Shift (0.5 kW) |  | 1 | GS-EVPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGS-EVAncillary EVPer Customer Summer Peak Reduction (%) | ID | GS-EV | Ancillary EV | Per Customer Summer Peak Reduction (%) | % of Peak | 75% | 0 |  | 1 | GS-EVPer Customer Summer Peak Reduction (%) | Market PotentialID
IDGS-EVAncillary EVPer Customer Winter Peak Reduction (kW) | ID | GS-EV | Ancillary EV | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | Update: Avista 2019 EVSE report claims 75% charging load reduction. Impact based on Res-EV impact/customer. OLD: Based on Avista research, expecting a 90% + Load Shift (0.5 kW) |  | 1 | GS-EVPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGS-EVAncillary EVPer Customer Winter Peak Reduction (%) | ID | GS-EV | Ancillary EV | Per Customer Winter Peak Reduction (%) | % of Peak | 75% | 0 |  | 1 | GS-EVPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceThird Party ContractsEvent Non-Performance Rate | ID | General Service | Third Party Contracts | Event Non-Performance Rate | % |  |  |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceThird Party ContractsPer Customer Summer Peak Reduction (kW) | ID | General Service | Third Party Contracts | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceThird Party ContractsPer Customer Summer Peak Reduction (%) | ID | General Service | Third Party Contracts | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceThird Party ContractsPer Customer Winter Peak Reduction (kW) | ID | General Service | Third Party Contracts | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceThird Party ContractsPer Customer Winter Peak Reduction (%) | ID | General Service | Third Party Contracts | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDLarge General ServiceThird Party ContractsEvent Non-Performance Rate | ID | Large General Service | Third Party Contracts | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Large General ServiceEvent Non-Performance Rate | Market PotentialID
IDLarge General ServiceThird Party ContractsPer Customer Summer Peak Reduction (kW) | ID | Large General Service | Third Party Contracts | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDLarge General ServiceThird Party ContractsPer Customer Summer Peak Reduction (%) | ID | Large General Service | Third Party Contracts | Per Customer Summer Peak Reduction (%) | % of Peak | 21% | weighted average from impacts in the following report: Impact Estimates from Aggregator Programs in California (Source: 2012 Statewide Load Impact Evaluation of California Aggregator Demand Response Programs Volume 1: Ex post and Ex ante Load Impacts; Christensen Associates Energy Consulting; April 1, 2013). |  | 1 | Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDLarge General ServiceThird Party ContractsPer Customer Winter Peak Reduction (kW) | ID | Large General Service | Third Party Contracts | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDLarge General ServiceThird Party ContractsPer Customer Winter Peak Reduction (%) | ID | Large General Service | Third Party Contracts | Per Customer Winter Peak Reduction (%) | % of Peak | 21% | weighted average from impacts in the following report: Impact Estimates from Aggregator Programs in California (Source: 2012 Statewide Load Impact Evaluation of California Aggregator Demand Response Programs Volume 1: Ex post and Ex ante Load Impacts; Christensen Associates Energy Consulting; April 1, 2013). |  | 1 | Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDExtra Large General ServiceThird Party ContractsEvent Non-Performance Rate | ID | Extra Large General Service | Third Party Contracts | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Extra Large General ServiceEvent Non-Performance Rate | Market PotentialID
IDExtra Large General ServiceThird Party ContractsPer Customer Summer Peak Reduction (kW) | ID | Extra Large General Service | Third Party Contracts | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDExtra Large General ServiceThird Party ContractsPer Customer Summer Peak Reduction (%) | ID | Extra Large General Service | Third Party Contracts | Per Customer Summer Peak Reduction (%) | % of Peak | 21% | weighted average from impacts in the following report: Impact Estimates from Aggregator Programs in California (Source: 2012 Statewide Load Impact Evaluation of California Aggregator Demand Response Programs Volume 1: Ex post and Ex ante Load Impacts; Christensen Associates Energy Consulting; April 1, 2013). |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDExtra Large General ServiceThird Party ContractsPer Customer Winter Peak Reduction (kW) | ID | Extra Large General Service | Third Party Contracts | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDExtra Large General ServiceThird Party ContractsPer Customer Winter Peak Reduction (%) | ID | Extra Large General Service | Third Party Contracts | Per Customer Winter Peak Reduction (%) | % of Peak | 21% | weighted average from impacts in the following report: Impact Estimates from Aggregator Programs in California (Source: 2012 Statewide Load Impact Evaluation of California Aggregator Demand Response Programs Volume 1: Ex post and Ex ante Load Impacts; Christensen Associates Energy Consulting; April 1, 2013). |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceAncillary Third PartyEvent Non-Performance Rate | ID | General Service | Ancillary Third Party | Event Non-Performance Rate | % |  |  |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceAncillary Third PartyPer Customer Summer Peak Reduction (kW) | ID | General Service | Ancillary Third Party | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceAncillary Third PartyPer Customer Summer Peak Reduction (%) | ID | General Service | Ancillary Third Party | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceAncillary Third PartyPer Customer Winter Peak Reduction (kW) | ID | General Service | Ancillary Third Party | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceAncillary Third PartyPer Customer Winter Peak Reduction (%) | ID | General Service | Ancillary Third Party | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDLarge General ServiceAncillary Third PartyEvent Non-Performance Rate | ID | Large General Service | Ancillary Third Party | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Large General ServiceEvent Non-Performance Rate | Market PotentialID
IDLarge General ServiceAncillary Third PartyPer Customer Summer Peak Reduction (kW) | ID | Large General Service | Ancillary Third Party | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDLarge General ServiceAncillary Third PartyPer Customer Summer Peak Reduction (%) | ID | Large General Service | Ancillary Third Party | Per Customer Summer Peak Reduction (%) | % of Peak | 15.75% | 75% of impact for ancillary |  | 1 | Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDLarge General ServiceAncillary Third PartyPer Customer Winter Peak Reduction (kW) | ID | Large General Service | Ancillary Third Party | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDLarge General ServiceAncillary Third PartyPer Customer Winter Peak Reduction (%) | ID | Large General Service | Ancillary Third Party | Per Customer Winter Peak Reduction (%) | % of Peak | 15.75% | 75% of impact for ancillary |  | 1 | Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDExtra Large General ServiceAncillary Third PartyEvent Non-Performance Rate | ID | Extra Large General Service | Ancillary Third Party | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Extra Large General ServiceEvent Non-Performance Rate | Market PotentialID
IDExtra Large General ServiceAncillary Third PartyPer Customer Summer Peak Reduction (kW) | ID | Extra Large General Service | Ancillary Third Party | Per Customer Summer Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDExtra Large General ServiceAncillary Third PartyPer Customer Summer Peak Reduction (%) | ID | Extra Large General Service | Ancillary Third Party | Per Customer Summer Peak Reduction (%) | % of Peak | 15.75% | 75% of impact for ancillary |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDExtra Large General ServiceAncillary Third PartyPer Customer Winter Peak Reduction (kW) | ID | Extra Large General Service | Ancillary Third Party | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | 0 |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDExtra Large General ServiceAncillary Third PartyPer Customer Winter Peak Reduction (%) | ID | Extra Large General Service | Ancillary Third Party | Per Customer Winter Peak Reduction (%) | % of Peak | 15.75% | 75% of impact for ancillary |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceThermal Energy StorageEvent Non-Performance Rate | ID | General Service | Thermal Energy Storage | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceThermal Energy StoragePer Customer Summer Peak Reduction (kW) | ID | General Service | Thermal Energy Storage | Per Customer Summer Peak Reduction (kW) | kW @meter | 1.68 | Ice Energy - Ice Bear Tech Specifications, https://www.ice-energy.com/wp-content/uploads/2016/03/ICE-BEAR-30-Product-Sheet.pdf |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceThermal Energy StoragePer Customer Summer Peak Reduction (%) | ID | General Service | Thermal Energy Storage | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceThermal Energy StoragePer Customer Winter Peak Reduction (kW) | ID | General Service | Thermal Energy Storage | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | Removed Winter Impacts |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceThermal Energy StoragePer Customer Winter Peak Reduction (%) | ID | General Service | Thermal Energy Storage | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDLarge General ServiceThermal Energy StorageEvent Non-Performance Rate | ID | Large General Service | Thermal Energy Storage | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Large General ServiceEvent Non-Performance Rate | Market PotentialID
IDLarge General ServiceThermal Energy StoragePer Customer Summer Peak Reduction (kW) | ID | Large General Service | Thermal Energy Storage | Per Customer Summer Peak Reduction (kW) | kW @meter | 8.4 | Ice Energy - Ice Bear Tech Specifications, https://www.ice-energy.com/wp-content/uploads/2016/03/ICE-BEAR-30-Product-Sheet.pdf |  | 1 | Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDLarge General ServiceThermal Energy StoragePer Customer Summer Peak Reduction (%) | ID | Large General Service | Thermal Energy Storage | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDLarge General ServiceThermal Energy StoragePer Customer Winter Peak Reduction (kW) | ID | Large General Service | Thermal Energy Storage | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | Removed Winter Impacts |  | 1 | Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDLarge General ServiceThermal Energy StoragePer Customer Winter Peak Reduction (%) | ID | Large General Service | Thermal Energy Storage | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDExtra Large General ServiceThermal Energy StorageEvent Non-Performance Rate | ID | Extra Large General Service | Thermal Energy Storage | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Extra Large General ServiceEvent Non-Performance Rate | Market PotentialID
IDExtra Large General ServiceThermal Energy StoragePer Customer Summer Peak Reduction (kW) | ID | Extra Large General Service | Thermal Energy Storage | Per Customer Summer Peak Reduction (kW) | kW @meter | 8.4 | Ice Energy - Ice Bear Tech Specifications, https://www.ice-energy.com/wp-content/uploads/2016/03/ICE-BEAR-30-Product-Sheet.pdf |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDExtra Large General ServiceThermal Energy StoragePer Customer Summer Peak Reduction (%) | ID | Extra Large General Service | Thermal Energy Storage | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDExtra Large General ServiceThermal Energy StoragePer Customer Winter Peak Reduction (kW) | ID | Extra Large General Service | Thermal Energy Storage | Per Customer Winter Peak Reduction (kW) | kW @meter | 0 | Removed Winter Impacts |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDExtra Large General ServiceThermal Energy StoragePer Customer Winter Peak Reduction (%) | ID | Extra Large General Service | Thermal Energy Storage | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialBattery Energy StorageEvent Non-Performance Rate | ID | Residential | Battery Energy Storage | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialBattery Energy StoragePer Customer Summer Peak Reduction (kW) | ID | Residential | Battery Energy Storage | Per Customer Summer Peak Reduction (kW) | kW @meter | 1.85 | NREL 2021: 5 kW battery * 86% round trip efficiency. Xcel Energy CO Renewable Battery Connect: 40% retention |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialBattery Energy StoragePer Customer Summer Peak Reduction (%) | ID | Residential | Battery Energy Storage | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialBattery Energy StoragePer Customer Winter Peak Reduction (kW) | ID | Residential | Battery Energy Storage | Per Customer Winter Peak Reduction (kW) | kW @meter | 2.44 | NREL 2021: 5 kW battery * 86% round trip efficiency. Xcel Energy CO Renewable Battery Connect: 40% retention |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialBattery Energy StoragePer Customer Winter Peak Reduction (%) | ID | Residential | Battery Energy Storage | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceBattery Energy StorageEvent Non-Performance Rate | ID | General Service | Battery Energy Storage | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceBattery Energy StoragePer Customer Summer Peak Reduction (kW) | ID | General Service | Battery Energy Storage | Per Customer Summer Peak Reduction (kW) | kW @meter | 2.58 | NREL 2021: 5 kW battery * 86% round trip efficiency. Xcel Energy CO Renewable Battery Connect: 40% retention |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceBattery Energy StoragePer Customer Summer Peak Reduction (%) | ID | General Service | Battery Energy Storage | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceBattery Energy StoragePer Customer Winter Peak Reduction (kW) | ID | General Service | Battery Energy Storage | Per Customer Winter Peak Reduction (kW) | kW @meter | 2.58 | NREL 2021: 5 kW battery * 86% round trip efficiency. Xcel Energy CO Renewable Battery Connect: 40% retention |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceBattery Energy StoragePer Customer Winter Peak Reduction (%) | ID | General Service | Battery Energy Storage | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDLarge General ServiceBattery Energy StorageEvent Non-Performance Rate | ID | Large General Service | Battery Energy Storage | Event Non-Performance Rate | % |  |  |  | 1 | Large General ServiceEvent Non-Performance Rate | Market PotentialID
IDLarge General ServiceBattery Energy StoragePer Customer Summer Peak Reduction (kW) | ID | Large General Service | Battery Energy Storage | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDLarge General ServiceBattery Energy StoragePer Customer Summer Peak Reduction (%) | ID | Large General Service | Battery Energy Storage | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDLarge General ServiceBattery Energy StoragePer Customer Winter Peak Reduction (kW) | ID | Large General Service | Battery Energy Storage | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDLarge General ServiceBattery Energy StoragePer Customer Winter Peak Reduction (%) | ID | Large General Service | Battery Energy Storage | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDExtra Large General ServiceBattery Energy StorageEvent Non-Performance Rate | ID | Extra Large General Service | Battery Energy Storage | Event Non-Performance Rate | % |  |  |  | 1 | Extra Large General ServiceEvent Non-Performance Rate | Market PotentialID
IDExtra Large General ServiceBattery Energy StoragePer Customer Summer Peak Reduction (kW) | ID | Extra Large General Service | Battery Energy Storage | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDExtra Large General ServiceBattery Energy StoragePer Customer Summer Peak Reduction (%) | ID | Extra Large General Service | Battery Energy Storage | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDExtra Large General ServiceBattery Energy StoragePer Customer Winter Peak Reduction (kW) | ID | Extra Large General Service | Battery Energy Storage | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDExtra Large General ServiceBattery Energy StoragePer Customer Winter Peak Reduction (%) | ID | Extra Large General Service | Battery Energy Storage | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialAncillary Battery StorageEvent Non-Performance Rate | ID | Residential | Ancillary Battery Storage | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialAncillary Battery StoragePer Customer Summer Peak Reduction (kW) | ID | Residential | Ancillary Battery Storage | Per Customer Summer Peak Reduction (kW) | kW @meter | 1.85 | Typical battery size for segment |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialAncillary Battery StoragePer Customer Summer Peak Reduction (%) | ID | Residential | Ancillary Battery Storage | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialAncillary Battery StoragePer Customer Winter Peak Reduction (kW) | ID | Residential | Ancillary Battery Storage | Per Customer Winter Peak Reduction (kW) | kW @meter | 2.44 | Typical battery size for segment |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialAncillary Battery StoragePer Customer Winter Peak Reduction (%) | ID | Residential | Ancillary Battery Storage | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceAncillary Battery StorageEvent Non-Performance Rate | ID | General Service | Ancillary Battery Storage | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceAncillary Battery StoragePer Customer Summer Peak Reduction (kW) | ID | General Service | Ancillary Battery Storage | Per Customer Summer Peak Reduction (kW) | kW @meter | 2.58 | Typical battery size for segment |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceAncillary Battery StoragePer Customer Summer Peak Reduction (%) | ID | General Service | Ancillary Battery Storage | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceAncillary Battery StoragePer Customer Winter Peak Reduction (kW) | ID | General Service | Ancillary Battery Storage | Per Customer Winter Peak Reduction (kW) | kW @meter | 2.58 | Typical battery size for segment |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceAncillary Battery StoragePer Customer Winter Peak Reduction (%) | ID | General Service | Ancillary Battery Storage | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDLarge General ServiceAncillary Battery StorageEvent Non-Performance Rate | ID | Large General Service | Ancillary Battery Storage | Event Non-Performance Rate | % |  |  |  | 1 | Large General ServiceEvent Non-Performance Rate | Market PotentialID
IDLarge General ServiceAncillary Battery StoragePer Customer Summer Peak Reduction (kW) | ID | Large General Service | Ancillary Battery Storage | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDLarge General ServiceAncillary Battery StoragePer Customer Summer Peak Reduction (%) | ID | Large General Service | Ancillary Battery Storage | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDLarge General ServiceAncillary Battery StoragePer Customer Winter Peak Reduction (kW) | ID | Large General Service | Ancillary Battery Storage | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDLarge General ServiceAncillary Battery StoragePer Customer Winter Peak Reduction (%) | ID | Large General Service | Ancillary Battery Storage | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDExtra Large General ServiceAncillary Battery StorageEvent Non-Performance Rate | ID | Extra Large General Service | Ancillary Battery Storage | Event Non-Performance Rate | % |  |  |  | 1 | Extra Large General ServiceEvent Non-Performance Rate | Market PotentialID
IDExtra Large General ServiceAncillary Battery StoragePer Customer Summer Peak Reduction (kW) | ID | Extra Large General Service | Ancillary Battery Storage | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDExtra Large General ServiceAncillary Battery StoragePer Customer Summer Peak Reduction (%) | ID | Extra Large General Service | Ancillary Battery Storage | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDExtra Large General ServiceAncillary Battery StoragePer Customer Winter Peak Reduction (kW) | ID | Extra Large General Service | Ancillary Battery Storage | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDExtra Large General ServiceAncillary Battery StoragePer Customer Winter Peak Reduction (%) | ID | Extra Large General Service | Ancillary Battery Storage | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialBehavioralEvent Non-Performance Rate | ID | Residential | Behavioral | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialBehavioralPer Customer Summer Peak Reduction (kW) | ID | Residential | Behavioral | Per Customer Summer Peak Reduction (kW) | kW @meter | 0% | hi participation case = 0.75% of low to account for lower potential customers |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialBehavioralPer Customer Summer Peak Reduction (%) | ID | Residential | Behavioral | Per Customer Summer Peak Reduction (%) | % of Peak | 2% | Opower documentation for BDR with Consumers and DTE |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialBehavioralPer Customer Winter Peak Reduction (kW) | ID | Residential | Behavioral | Per Customer Winter Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialBehavioralPer Customer Winter Peak Reduction (%) | ID | Residential | Behavioral | Per Customer Winter Peak Reduction (%) | % of Peak | 2% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inEvent Non-Performance Rate | ID | Residential | Pilot-Time-of-Use Opt-in | Event Non-Performance Rate | % | 0% | None - should be in eval'd number. |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inPer Customer Summer Peak Reduction (kW) | ID | Residential | Pilot-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inPer Customer Summer Peak Reduction (%) | ID | Residential | Pilot-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | Brattle Analysis and Estimate - Pacificorp 2019 opt-in and opt-out scenarios |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inPer Customer Winter Peak Reduction (kW) | ID | Residential | Pilot-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inPer Customer Winter Peak Reduction (%) | ID | Residential | Pilot-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | Assume 50% of Summer impacts. Brattle Analysis and Estimate - Negative impacts in Winter set to zero in Eastern states. |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inEvent Non-Performance Rate | ID | General Service | Pilot-Time-of-Use Opt-in | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inPer Customer Summer Peak Reduction (kW) | ID | General Service | Pilot-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inPer Customer Summer Peak Reduction (%) | ID | General Service | Pilot-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | Brattle Analysis and Estimate - Pacificorp 2019 opt-in and opt-out scenarios |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inPer Customer Winter Peak Reduction (kW) | ID | General Service | Pilot-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inPer Customer Winter Peak Reduction (%) | ID | General Service | Pilot-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | Assume 50% of Summer impacts. |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inEvent Non-Performance Rate | ID | Residential | Parent-Time-of-Use Opt-in | Event Non-Performance Rate | % | 0% | None - should be in eval'd number. |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inPer Customer Summer Peak Reduction (kW) | ID | Residential | Parent-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inPer Customer Summer Peak Reduction (%) | ID | Residential | Parent-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (%) | % of Peak | 4% | 2024 Avista Update |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inPer Customer Winter Peak Reduction (kW) | ID | Residential | Parent-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inPer Customer Winter Peak Reduction (%) | ID | Residential | Parent-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (%) | % of Peak | 1.5% | 2024 Avista Update |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inEvent Non-Performance Rate | ID | General Service | Parent-Time-of-Use Opt-in | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inPer Customer Summer Peak Reduction (kW) | ID | General Service | Parent-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inPer Customer Summer Peak Reduction (%) | ID | General Service | Parent-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (%) | % of Peak | 0.2% | Brattle Analysis and Estimate - Pacificorp 2019 opt-in and opt-out scenarios |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inPer Customer Winter Peak Reduction (kW) | ID | General Service | Parent-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inPer Customer Winter Peak Reduction (%) | ID | General Service | Parent-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (%) | % of Peak | 0.1% | Assume 50% of Summer impacts. |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inEvent Non-Performance Rate | ID | Large General Service | Parent-Time-of-Use Opt-in | Event Non-Performance Rate | % |  |  |  | 1 | Large General ServiceEvent Non-Performance Rate | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inPer Customer Summer Peak Reduction (kW) | ID | Large General Service | Parent-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inPer Customer Summer Peak Reduction (%) | ID | Large General Service | Parent-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inPer Customer Winter Peak Reduction (kW) | ID | Large General Service | Parent-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inPer Customer Winter Peak Reduction (%) | ID | Large General Service | Parent-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inEvent Non-Performance Rate | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Event Non-Performance Rate | % |  |  |  | 1 | Extra Large General ServiceEvent Non-Performance Rate | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inPer Customer Summer Peak Reduction (kW) | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inPer Customer Summer Peak Reduction (%) | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inPer Customer Winter Peak Reduction (kW) | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inPer Customer Winter Peak Reduction (%) | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialTime-of-Use Opt-OutEvent Non-Performance Rate | ID | Residential | Time-of-Use Opt-Out | Event Non-Performance Rate | % | 0% | None - should be in eval'd number. |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialTime-of-Use Opt-OutPer Customer Summer Peak Reduction (kW) | ID | Residential | Time-of-Use Opt-Out | Per Customer Summer Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialTime-of-Use Opt-OutPer Customer Summer Peak Reduction (%) | ID | Residential | Time-of-Use Opt-Out | Per Customer Summer Peak Reduction (%) | % of Peak | 1.5% | 2024 Avista Update |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialTime-of-Use Opt-OutPer Customer Winter Peak Reduction (kW) | ID | Residential | Time-of-Use Opt-Out | Per Customer Winter Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialTime-of-Use Opt-OutPer Customer Winter Peak Reduction (%) | ID | Residential | Time-of-Use Opt-Out | Per Customer Winter Peak Reduction (%) | % of Peak | 0.2% | 2024 Avista Update |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutEvent Non-Performance Rate | ID | General Service | Time-of-Use Opt-Out | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutPer Customer Summer Peak Reduction (kW) | ID | General Service | Time-of-Use Opt-Out | Per Customer Summer Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutPer Customer Summer Peak Reduction (%) | ID | General Service | Time-of-Use Opt-Out | Per Customer Summer Peak Reduction (%) | % of Peak | 0.2% | Brattle Analysis and Estimate - Pacificorp 2019 opt-in and opt-out scenarios |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutPer Customer Winter Peak Reduction (kW) | ID | General Service | Time-of-Use Opt-Out | Per Customer Winter Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutPer Customer Winter Peak Reduction (%) | ID | General Service | Time-of-Use Opt-Out | Per Customer Winter Peak Reduction (%) | % of Peak | 0.1% | Assume 50% of Summer impacts. |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutEvent Non-Performance Rate | ID | Large General Service | Time-of-Use Opt-Out | Event Non-Performance Rate | % |  |  |  | 1 | Large General ServiceEvent Non-Performance Rate | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutPer Customer Summer Peak Reduction (kW) | ID | Large General Service | Time-of-Use Opt-Out | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutPer Customer Summer Peak Reduction (%) | ID | Large General Service | Time-of-Use Opt-Out | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutPer Customer Winter Peak Reduction (kW) | ID | Large General Service | Time-of-Use Opt-Out | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutPer Customer Winter Peak Reduction (%) | ID | Large General Service | Time-of-Use Opt-Out | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutEvent Non-Performance Rate | ID | Extra Large General Service | Time-of-Use Opt-Out | Event Non-Performance Rate | % |  |  |  | 1 | Extra Large General ServiceEvent Non-Performance Rate | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutPer Customer Summer Peak Reduction (kW) | ID | Extra Large General Service | Time-of-Use Opt-Out | Per Customer Summer Peak Reduction (kW) | kW @meter |  |  |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutPer Customer Summer Peak Reduction (%) | ID | Extra Large General Service | Time-of-Use Opt-Out | Per Customer Summer Peak Reduction (%) | % of Peak |  |  |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutPer Customer Winter Peak Reduction (kW) | ID | Extra Large General Service | Time-of-Use Opt-Out | Per Customer Winter Peak Reduction (kW) | kW @meter |  |  |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutPer Customer Winter Peak Reduction (%) | ID | Extra Large General Service | Time-of-Use Opt-Out | Per Customer Winter Peak Reduction (%) | % of Peak |  |  |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inEvent Non-Performance Rate | ID | GS-EV | Electric Vehicle TOU Opt-in | Event Non-Performance Rate | % | 0% | 0 |  | 1 | GS-EVEvent Non-Performance Rate | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inPer Customer Summer Peak Reduction (kW) | ID | GS-EV | Electric Vehicle TOU Opt-in | Per Customer Summer Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | GS-EVPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inPer Customer Summer Peak Reduction (%) | ID | GS-EV | Electric Vehicle TOU Opt-in | Per Customer Summer Peak Reduction (%) | % of Peak | 100% | 2024 Avista Update: of total EV load instead of total HH load |  | 1 | GS-EVPer Customer Summer Peak Reduction (%) | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inPer Customer Winter Peak Reduction (kW) | ID | GS-EV | Electric Vehicle TOU Opt-in | Per Customer Winter Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | GS-EVPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inPer Customer Winter Peak Reduction (%) | ID | GS-EV | Electric Vehicle TOU Opt-in | Per Customer Winter Peak Reduction (%) | % of Peak | 100% | 2024 Avista Update: of total EV load instead of total HH load |  | 1 | GS-EVPer Customer Winter Peak Reduction (%) | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inEvent Non-Performance Rate | ID | LGS-EV | Electric Vehicle TOU Opt-in | Event Non-Performance Rate | % | 0% | 0 |  | 1 | LGS-EVEvent Non-Performance Rate | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inPer Customer Summer Peak Reduction (kW) | ID | LGS-EV | Electric Vehicle TOU Opt-in | Per Customer Summer Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | LGS-EVPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inPer Customer Summer Peak Reduction (%) | ID | LGS-EV | Electric Vehicle TOU Opt-in | Per Customer Summer Peak Reduction (%) | % of Peak | 100% | 2024 Avista Update: of total EV load instead of total HH load |  | 1 | LGS-EVPer Customer Summer Peak Reduction (%) | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inPer Customer Winter Peak Reduction (kW) | ID | LGS-EV | Electric Vehicle TOU Opt-in | Per Customer Winter Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | LGS-EVPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inPer Customer Winter Peak Reduction (%) | ID | LGS-EV | Electric Vehicle TOU Opt-in | Per Customer Winter Peak Reduction (%) | % of Peak | 100% | 2024 Avista Update: of total EV load instead of total HH load |  | 1 | LGS-EVPer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialPilot-Peak Time RebateEvent Non-Performance Rate | ID | Residential | Pilot-Peak Time Rebate | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialPilot-Peak Time RebatePer Customer Summer Peak Reduction (kW) | ID | Residential | Pilot-Peak Time Rebate | Per Customer Summer Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialPilot-Peak Time RebatePer Customer Summer Peak Reduction (%) | ID | Residential | Pilot-Peak Time Rebate | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: 0.159 or 8.2% in summer, 0.134 or 7.1% in winter |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialPilot-Peak Time RebatePer Customer Winter Peak Reduction (kW) | ID | Residential | Pilot-Peak Time Rebate | Per Customer Winter Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialPilot-Peak Time RebatePer Customer Winter Peak Reduction (%) | ID | Residential | Pilot-Peak Time Rebate | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: 0.159 or 8.2% in summer, 0.134 or 7.1% in winter |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServicePilot-Peak Time RebateEvent Non-Performance Rate | ID | General Service | Pilot-Peak Time Rebate | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServicePilot-Peak Time RebatePer Customer Summer Peak Reduction (kW) | ID | General Service | Pilot-Peak Time Rebate | Per Customer Summer Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServicePilot-Peak Time RebatePer Customer Summer Peak Reduction (%) | ID | General Service | Pilot-Peak Time Rebate | Per Customer Summer Peak Reduction (%) | % of Peak | 0% | Assumes half residential estimates from PGE Flex 2.0 PTR pilot evaliation 2021 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServicePilot-Peak Time RebatePer Customer Winter Peak Reduction (kW) | ID | General Service | Pilot-Peak Time Rebate | Per Customer Winter Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServicePilot-Peak Time RebatePer Customer Winter Peak Reduction (%) | ID | General Service | Pilot-Peak Time Rebate | Per Customer Winter Peak Reduction (%) | % of Peak | 0% | Assumes half residential estimates from PGE Flex 2.0 PTR pilot evaliation 2021 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDResidentialParent-Peak Time RebateEvent Non-Performance Rate | ID | Residential | Parent-Peak Time Rebate | Event Non-Performance Rate | % | 0% | 0 |  | 1 | ResidentialEvent Non-Performance Rate | Market PotentialID
IDResidentialParent-Peak Time RebatePer Customer Summer Peak Reduction (kW) | ID | Residential | Parent-Peak Time Rebate | Per Customer Summer Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | ResidentialPer Customer Summer Peak Reduction (kW) | Market PotentialID
IDResidentialParent-Peak Time RebatePer Customer Summer Peak Reduction (%) | ID | Residential | Parent-Peak Time Rebate | Per Customer Summer Peak Reduction (%) | % of Peak | 8.2% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: 0.159 or 8.2% in summer, 0.134 or 7.1% in winter |  | 1 | ResidentialPer Customer Summer Peak Reduction (%) | Market PotentialID
IDResidentialParent-Peak Time RebatePer Customer Winter Peak Reduction (kW) | ID | Residential | Parent-Peak Time Rebate | Per Customer Winter Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | ResidentialPer Customer Winter Peak Reduction (kW) | Market PotentialID
IDResidentialParent-Peak Time RebatePer Customer Winter Peak Reduction (%) | ID | Residential | Parent-Peak Time Rebate | Per Customer Winter Peak Reduction (%) | % of Peak | 7.1% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: 0.159 or 8.2% in summer, 0.134 or 7.1% in winter |  | 1 | ResidentialPer Customer Winter Peak Reduction (%) | Market PotentialID
IDGeneral ServiceParent-Peak Time RebateEvent Non-Performance Rate | ID | General Service | Parent-Peak Time Rebate | Event Non-Performance Rate | % | 0% | 0 |  | 1 | General ServiceEvent Non-Performance Rate | Market PotentialID
IDGeneral ServiceParent-Peak Time RebatePer Customer Summer Peak Reduction (kW) | ID | General Service | Parent-Peak Time Rebate | Per Customer Summer Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceParent-Peak Time RebatePer Customer Summer Peak Reduction (%) | ID | General Service | Parent-Peak Time Rebate | Per Customer Summer Peak Reduction (%) | % of Peak | 4.1% | Assumes half residential estimates from PGE Flex 2.0 PTR pilot evaliation 2021 |  | 1 | General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDGeneral ServiceParent-Peak Time RebatePer Customer Winter Peak Reduction (kW) | ID | General Service | Parent-Peak Time Rebate | Per Customer Winter Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDGeneral ServiceParent-Peak Time RebatePer Customer Winter Peak Reduction (%) | ID | General Service | Parent-Peak Time Rebate | Per Customer Winter Peak Reduction (%) | % of Peak | 3.55% | Assumes half residential estimates from PGE Flex 2.0 PTR pilot evaliation 2021 |  | 1 | General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesEvent Non-Performance Rate | ID | Large General Service | Variable Peak Pricing Rates | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Large General ServiceEvent Non-Performance Rate | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesPer Customer Summer Peak Reduction (kW) | ID | Large General Service | Variable Peak Pricing Rates | Per Customer Summer Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesPer Customer Summer Peak Reduction (%) | ID | Large General Service | Variable Peak Pricing Rates | Per Customer Summer Peak Reduction (%) | % of Peak | 4% | OG&E 2017 Smart Hours Study - 4% for an average CPE day for VPP only customers without a smart thermostat |  | 1 | Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesPer Customer Winter Peak Reduction (kW) | ID | Large General Service | Variable Peak Pricing Rates | Per Customer Winter Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesPer Customer Winter Peak Reduction (%) | ID | Large General Service | Variable Peak Pricing Rates | Per Customer Winter Peak Reduction (%) | % of Peak | 3% | 0 |  | 1 | Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesEvent Non-Performance Rate | ID | Extra Large General Service | Variable Peak Pricing Rates | Event Non-Performance Rate | % | 0% | 0 |  | 1 | Extra Large General ServiceEvent Non-Performance Rate | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesPer Customer Summer Peak Reduction (kW) | ID | Extra Large General Service | Variable Peak Pricing Rates | Per Customer Summer Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesPer Customer Summer Peak Reduction (%) | ID | Extra Large General Service | Variable Peak Pricing Rates | Per Customer Summer Peak Reduction (%) | % of Peak | 4% | OG&E 2017 Smart Hours Study - 4% for an average CPE day for VPP only customers without a smart thermostat |  | 1 | Extra Large General ServicePer Customer Summer Peak Reduction (%) | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesPer Customer Winter Peak Reduction (kW) | ID | Extra Large General Service | Variable Peak Pricing Rates | Per Customer Winter Peak Reduction (kW) | kW @meter | 0% | 0 |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesPer Customer Winter Peak Reduction (%) | ID | Extra Large General Service | Variable Peak Pricing Rates | Per Customer Winter Peak Reduction (%) | % of Peak | 3% | 0 |  | 1 | Extra Large General ServicePer Customer Winter Peak Reduction (%) | Market PotentialID

## CEInput
Key | State | Customer Class | Option | Data Element | Unit | Market Potential | Comments from Input Generator | Copy & Paste Values to Left into Model | Row Lookup | Column Lookup
WAResidentialDLC Central ACSummer DR Event Hours | WA | Residential | DLC Central AC | Summer DR Event Hours | hours/year | 50 | Current PC Cool Keeper program allows for max 100 hours of curtailment. |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialDLC Central ACWinter DR Event Hours | WA | Residential | DLC Central AC | Winter DR Event Hours | hours/year | 0 | 0 |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialDLC Central ACAnnual O&M Cost | WA | Residential | DLC Central AC | Annual O&M Cost | $/participant/year | 13 | Assume 5% of equipment + install costs. |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialDLC Central ACAnnual O&M Cost per MW | WA | Residential | DLC Central AC | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialDLC Central ACAnnual Program Administration Cost | WA | Residential | DLC Central AC | Annual Program Administration Cost | $/yr | 51953.4223 | Share of Cost as noted in table at right |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialDLC Central ACCost of Equip + Install | WA | Residential | DLC Central AC | Cost of Equip + Install | $/tech | 260 | $100 installation cost. Idaho Power at 10,000 quantity pays $160 per switch. It's believed Avista volumes would be the same or less per order, making the cost $160 or greater. |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialDLC Central ACCost of Equip + Install (per kW basis) | WA | Residential | DLC Central AC | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialDLC Central ACDe-rate | WA | Residential | DLC Central AC | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialDLC Central ACNet to Gross Ratio (free ridership) | WA | Residential | DLC Central AC | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialDLC Central ACPer Customer Annual Marketing/Recruitment Cost | WA | Residential | DLC Central AC | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Utah $50, All others $60 (20% higher) |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialDLC Central ACPer Participant Annual Incentive | WA | Residential | DLC Central AC | Per Participant Annual Incentive | $/participant/year | 20 | $20 is the incentive level per participating unit. No. of units per average participant is 1.059. Aligns with ID Power rebate. |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialDLC Central ACPer kW Annual Incentive | WA | Residential | DLC Central AC | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialDLC Central ACProgram Development Cost | WA | Residential | DLC Central AC | Program Development Cost | $/program | 43294.5186 | 0 |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialDLC Central ACProgram Life | WA | Residential | DLC Central AC | Program Life | years | 8 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialDLC Central ACProgram Start Year | WA | Residential | DLC Central AC | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServiceDLC Central ACSummer DR Event Hours | WA | General Service | DLC Central AC | Summer DR Event Hours | hours/year | 50 | Current PC Cool Keeper program allows for max 100 hours of curtailment. |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceDLC Central ACWinter DR Event Hours | WA | General Service | DLC Central AC | Winter DR Event Hours | hours/year | 0 | 0 |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceDLC Central ACAnnual O&M Cost | WA | General Service | DLC Central AC | Annual O&M Cost | $/participant/year | 13 | Assume 5% of equipment + install costs. |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceDLC Central ACAnnual O&M Cost per MW | WA | General Service | DLC Central AC | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceDLC Central ACAnnual Program Administration Cost | WA | General Service | DLC Central AC | Annual Program Administration Cost | $/yr | 4969.0628 | Share of Cost as noted in table at right |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceDLC Central ACCost of Equip + Install | WA | General Service | DLC Central AC | Cost of Equip + Install | $/tech | 260 | $100 installation cost. Idaho Power at 10,000 quantity pays $160 per switch. It's believed Avista volumes would be the same or less per order, making the cost $160 or greater. |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceDLC Central ACCost of Equip + Install (per kW basis) | WA | General Service | DLC Central AC | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceDLC Central ACDe-rate | WA | General Service | DLC Central AC | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceDLC Central ACNet to Gross Ratio (free ridership) | WA | General Service | DLC Central AC | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceDLC Central ACPer Customer Annual Marketing/Recruitment Cost | WA | General Service | DLC Central AC | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | 25% Higher than Residential |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceDLC Central ACPer Participant Annual Incentive | WA | General Service | DLC Central AC | Per Participant Annual Incentive | $/participant/year | 38 | Assumed participants have less than 5.5 tons of AC unit. Incentive level provided by PacifiCorp. |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceDLC Central ACPer kW Annual Incentive | WA | General Service | DLC Central AC | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceDLC Central ACProgram Development Cost | WA | General Service | DLC Central AC | Program Development Cost | $/program | 4140.8857 | 0 |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceDLC Central ACProgram Life | WA | General Service | DLC Central AC | Program Life | years | 8 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceDLC Central ACProgram Start Year | WA | General Service | DLC Central AC | Program Start Year | year | 2026 | 0 |  | General ServiceProgram Start Year | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingSummer DR Event Hours | WA | Residential | DLC Smart Thermostats - Cooling | Summer DR Event Hours | hours/year | 36 | 2016 M&V Report Event Hours |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingWinter DR Event Hours | WA | Residential | DLC Smart Thermostats - Cooling | Winter DR Event Hours | hours/year | 0 | 0 |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingAnnual O&M Cost | WA | Residential | DLC Smart Thermostats - Cooling | Annual O&M Cost | $/participant/year | 164 | 2024 Avista Update: $44 + $10/month fee per tstat |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingAnnual O&M Cost per MW | WA | Residential | DLC Smart Thermostats - Cooling | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingAnnual Program Administration Cost | WA | Residential | DLC Smart Thermostats - Cooling | Annual Program Administration Cost | $/yr | 51953.4223 | 0 |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingCost of Equip + Install | WA | Residential | DLC Smart Thermostats - Cooling | Cost of Equip + Install | $/tech | 0 | Bring Your Own Thermostat program |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingCost of Equip + Install (per kW basis) | WA | Residential | DLC Smart Thermostats - Cooling | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingDe-rate | WA | Residential | DLC Smart Thermostats - Cooling | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingNet to Gross Ratio (free ridership) | WA | Residential | DLC Smart Thermostats - Cooling | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingPer Customer Annual Marketing/Recruitment Cost | WA | Residential | DLC Smart Thermostats - Cooling | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Utah $50, All others $60 (20% higher) |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingPer Participant Annual Incentive | WA | Residential | DLC Smart Thermostats - Cooling | Per Participant Annual Incentive | $/participant/year | 20 | Assume $20 per year per system, same as CAC DLC. |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingPer kW Annual Incentive | WA | Residential | DLC Smart Thermostats - Cooling | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingProgram Development Cost | WA | Residential | DLC Smart Thermostats - Cooling | Program Development Cost | $/program | 202041.0869 | Share of Cost as noted in table at right |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingProgram Life | WA | Residential | DLC Smart Thermostats - Cooling | Program Life | years | 10 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialDLC Smart Thermostats - CoolingProgram Start Year | WA | Residential | DLC Smart Thermostats - Cooling | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingSummer DR Event Hours | WA | General Service | DLC Smart Thermostats - Cooling | Summer DR Event Hours | hours/year | 36 | 2016 M&V Report Event Hours |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingWinter DR Event Hours | WA | General Service | DLC Smart Thermostats - Cooling | Winter DR Event Hours | hours/year | 0 | 0 |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingAnnual O&M Cost | WA | General Service | DLC Smart Thermostats - Cooling | Annual O&M Cost | $/participant/year | 164 | 2024 Avista Update: $44 + $10/month fee per tstat |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingAnnual O&M Cost per MW | WA | General Service | DLC Smart Thermostats - Cooling | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingAnnual Program Administration Cost | WA | General Service | DLC Smart Thermostats - Cooling | Annual Program Administration Cost | $/yr | 4969.0628 | 0 |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingCost of Equip + Install | WA | General Service | DLC Smart Thermostats - Cooling | Cost of Equip + Install | $/tech | 0 | Bring Your Own Thermostat program |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingCost of Equip + Install (per kW basis) | WA | General Service | DLC Smart Thermostats - Cooling | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingDe-rate | WA | General Service | DLC Smart Thermostats - Cooling | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingNet to Gross Ratio (free ridership) | WA | General Service | DLC Smart Thermostats - Cooling | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingPer Customer Annual Marketing/Recruitment Cost | WA | General Service | DLC Smart Thermostats - Cooling | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | Utah $50, All others $60 (25% higher) |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingPer Participant Annual Incentive | WA | General Service | DLC Smart Thermostats - Cooling | Per Participant Annual Incentive | $/participant/year | 20 | Assume $20 per year per system, same as CAC DLC. |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingPer kW Annual Incentive | WA | General Service | DLC Smart Thermostats - Cooling | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingProgram Development Cost | WA | General Service | DLC Smart Thermostats - Cooling | Program Development Cost | $/program | 19324.1332 | Share of Cost as noted in table at right |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingProgram Life | WA | General Service | DLC Smart Thermostats - Cooling | Program Life | years | 10 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - CoolingProgram Start Year | WA | General Service | DLC Smart Thermostats - Cooling | Program Start Year | year | 2026 | 0 |  | General ServiceProgram Start Year | Market PotentialWA
WAResidentialAncillary CoolingSummer DR Event Hours | WA | Residential | Ancillary Cooling | Summer DR Event Hours | hours/year | 36 | 2016 M&V Report Event Hours |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialAncillary CoolingWinter DR Event Hours | WA | Residential | Ancillary Cooling | Winter DR Event Hours | hours/year | 0 | 0 |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialAncillary CoolingAnnual O&M Cost | WA | Residential | Ancillary Cooling | Annual O&M Cost | $/participant/year | 0 | Zero for Ancillary |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialAncillary CoolingAnnual O&M Cost per MW | WA | Residential | Ancillary Cooling | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialAncillary CoolingAnnual Program Administration Cost | WA | Residential | Ancillary Cooling | Annual Program Administration Cost | $/yr | 17317.8074 | Half for Ancillary- tied to participation reduction from parent program |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialAncillary CoolingCost of Equip + Install | WA | Residential | Ancillary Cooling | Cost of Equip + Install | $/tech | 0 | BYOT |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialAncillary CoolingCost of Equip + Install (per kW basis) | WA | Residential | Ancillary Cooling | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialAncillary CoolingDe-rate | WA | Residential | Ancillary Cooling | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialAncillary CoolingNet to Gross Ratio (free ridership) | WA | Residential | Ancillary Cooling | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialAncillary CoolingPer Customer Annual Marketing/Recruitment Cost | WA | Residential | Ancillary Cooling | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Utah $50, All others $60 (20% higher) |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialAncillary CoolingPer Participant Annual Incentive | WA | Residential | Ancillary Cooling | Per Participant Annual Incentive | $/participant/year | 20 | Assume $20 per year per system, same as CAC DLC. Adding $20 to account for ancillary service option |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialAncillary CoolingPer kW Annual Incentive | WA | Residential | Ancillary Cooling | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialAncillary CoolingProgram Development Cost | WA | Residential | Ancillary Cooling | Program Development Cost | $/program | 21647.2593 | Half for Ancillary- tied to participation reduction from parent program |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialAncillary CoolingProgram Life | WA | Residential | Ancillary Cooling | Program Life | years | 10 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialAncillary CoolingProgram Start Year | WA | Residential | Ancillary Cooling | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServiceAncillary CoolingSummer DR Event Hours | WA | General Service | Ancillary Cooling | Summer DR Event Hours | hours/year | 36 | 2016 M&V Report Event Hours |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceAncillary CoolingWinter DR Event Hours | WA | General Service | Ancillary Cooling | Winter DR Event Hours | hours/year | 0 | 0 |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceAncillary CoolingAnnual O&M Cost | WA | General Service | Ancillary Cooling | Annual O&M Cost | $/participant/year | 0 | Zero since part of parent program |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceAncillary CoolingAnnual O&M Cost per MW | WA | General Service | Ancillary Cooling | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceAncillary CoolingAnnual Program Administration Cost | WA | General Service | Ancillary Cooling | Annual Program Administration Cost | $/yr | 1656.3543 | Half for Ancillary- tied to participation reduction from parent program |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceAncillary CoolingCost of Equip + Install | WA | General Service | Ancillary Cooling | Cost of Equip + Install | $/tech | 0 | Bring Your Own Thermostat program |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceAncillary CoolingCost of Equip + Install (per kW basis) | WA | General Service | Ancillary Cooling | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceAncillary CoolingDe-rate | WA | General Service | Ancillary Cooling | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceAncillary CoolingNet to Gross Ratio (free ridership) | WA | General Service | Ancillary Cooling | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceAncillary CoolingPer Customer Annual Marketing/Recruitment Cost | WA | General Service | Ancillary Cooling | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | Utah $50, All others $60 (25% higher) |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceAncillary CoolingPer Participant Annual Incentive | WA | General Service | Ancillary Cooling | Per Participant Annual Incentive | $/participant/year | 20 | Assume $20 per year per system, same as CAC DLC. Adding $20 to account for ancillary service option |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceAncillary CoolingPer kW Annual Incentive | WA | General Service | Ancillary Cooling | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceAncillary CoolingProgram Development Cost | WA | General Service | Ancillary Cooling | Program Development Cost | $/program | 2070.4428 | Half for Ancillary- tied to participation reduction from parent program |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceAncillary CoolingProgram Life | WA | General Service | Ancillary Cooling | Program Life | years | 10 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceAncillary CoolingProgram Start Year | WA | General Service | Ancillary Cooling | Program Start Year | year | 2026 | 0 |  | General ServiceProgram Start Year | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingSummer DR Event Hours | WA | Residential | DLC Smart Thermostats - Heating | Summer DR Event Hours | hours/year | 0 | 0 |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingWinter DR Event Hours | WA | Residential | DLC Smart Thermostats - Heating | Winter DR Event Hours | hours/year | 36 | 2016 M&V Report Event Hours |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingAnnual O&M Cost | WA | Residential | DLC Smart Thermostats - Heating | Annual O&M Cost | $/participant/year | 0 | Program would piggy-back off of Thermostats-Cooling and share those costs |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingAnnual O&M Cost per MW | WA | Residential | DLC Smart Thermostats - Heating | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingAnnual Program Administration Cost | WA | Residential | DLC Smart Thermostats - Heating | Annual Program Administration Cost | $/yr | 0 | Program would piggy-back off of Thermostats-Cooling and share those costs |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingCost of Equip + Install | WA | Residential | DLC Smart Thermostats - Heating | Cost of Equip + Install | $/tech | 0 | Bring your own thermostat program |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingCost of Equip + Install (per kW basis) | WA | Residential | DLC Smart Thermostats - Heating | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingDe-rate | WA | Residential | DLC Smart Thermostats - Heating | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingNet to Gross Ratio (free ridership) | WA | Residential | DLC Smart Thermostats - Heating | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingPer Customer Annual Marketing/Recruitment Cost | WA | Residential | DLC Smart Thermostats - Heating | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Utah $50, All others $60 (20% higher) |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingPer Participant Annual Incentive | WA | Residential | DLC Smart Thermostats - Heating | Per Participant Annual Incentive | $/participant/year | 20 | Assume $20 per year per system, same as CAC DLC. |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingPer kW Annual Incentive | WA | Residential | DLC Smart Thermostats - Heating | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingProgram Development Cost | WA | Residential | DLC Smart Thermostats - Heating | Program Development Cost | $/program | 0 | Program would piggy-back off of Thermostats-Cooling and share those costs |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingProgram Life | WA | Residential | DLC Smart Thermostats - Heating | Program Life | years | 10 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialDLC Smart Thermostats - HeatingProgram Start Year | WA | Residential | DLC Smart Thermostats - Heating | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingSummer DR Event Hours | WA | General Service | DLC Smart Thermostats - Heating | Summer DR Event Hours | hours/year | 0 | 0 |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingWinter DR Event Hours | WA | General Service | DLC Smart Thermostats - Heating | Winter DR Event Hours | hours/year | 36 | 2016 M&V Report Event Hours |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingAnnual O&M Cost | WA | General Service | DLC Smart Thermostats - Heating | Annual O&M Cost | $/participant/year | 0 | Program would piggy-back off of Thermostats-Cooling and share those costs |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingAnnual O&M Cost per MW | WA | General Service | DLC Smart Thermostats - Heating | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingAnnual Program Administration Cost | WA | General Service | DLC Smart Thermostats - Heating | Annual Program Administration Cost | $/yr | 0 | Program would piggy-back off of Thermostats-Cooling and share those costs |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingCost of Equip + Install | WA | General Service | DLC Smart Thermostats - Heating | Cost of Equip + Install | $/tech | 0 | Bring your own thermostat program |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingCost of Equip + Install (per kW basis) | WA | General Service | DLC Smart Thermostats - Heating | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingDe-rate | WA | General Service | DLC Smart Thermostats - Heating | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingNet to Gross Ratio (free ridership) | WA | General Service | DLC Smart Thermostats - Heating | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingPer Customer Annual Marketing/Recruitment Cost | WA | General Service | DLC Smart Thermostats - Heating | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | Utah $50, All others $60 (25% higher) |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingPer Participant Annual Incentive | WA | General Service | DLC Smart Thermostats - Heating | Per Participant Annual Incentive | $/participant/year | 20 | Assume $20 per year per system, same as CAC DLC. |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingPer kW Annual Incentive | WA | General Service | DLC Smart Thermostats - Heating | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingProgram Development Cost | WA | General Service | DLC Smart Thermostats - Heating | Program Development Cost | $/program | 0 | Program would piggy-back off of Thermostats-Cooling and share those costs |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingProgram Life | WA | General Service | DLC Smart Thermostats - Heating | Program Life | years | 10 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceDLC Smart Thermostats - HeatingProgram Start Year | WA | General Service | DLC Smart Thermostats - Heating | Program Start Year | year | 2026 | 0 |  | General ServiceProgram Start Year | Market PotentialWA
WAResidentialAncillary HeatingSummer DR Event Hours | WA | Residential | Ancillary Heating | Summer DR Event Hours | hours/year | 0 | 0 |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialAncillary HeatingWinter DR Event Hours | WA | Residential | Ancillary Heating | Winter DR Event Hours | hours/year | 36 | 2016 M&V Report Event Hours |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialAncillary HeatingAnnual O&M Cost | WA | Residential | Ancillary Heating | Annual O&M Cost | $/participant/year | 0 | Zero for Ancillary |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialAncillary HeatingAnnual O&M Cost per MW | WA | Residential | Ancillary Heating | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialAncillary HeatingAnnual Program Administration Cost | WA | Residential | Ancillary Heating | Annual Program Administration Cost | $/yr | 0 | Program would piggy-back off of Ancillary-Cooling and share those costs |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialAncillary HeatingCost of Equip + Install | WA | Residential | Ancillary Heating | Cost of Equip + Install | $/tech | 0 | Bring your own thermostat program |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialAncillary HeatingCost of Equip + Install (per kW basis) | WA | Residential | Ancillary Heating | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialAncillary HeatingDe-rate | WA | Residential | Ancillary Heating | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialAncillary HeatingNet to Gross Ratio (free ridership) | WA | Residential | Ancillary Heating | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialAncillary HeatingPer Customer Annual Marketing/Recruitment Cost | WA | Residential | Ancillary Heating | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Utah $50, All others $60 (20% higher) |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialAncillary HeatingPer Participant Annual Incentive | WA | Residential | Ancillary Heating | Per Participant Annual Incentive | $/participant/year | 20 | Assume $20 per year per system, same as CAC DLC. |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialAncillary HeatingPer kW Annual Incentive | WA | Residential | Ancillary Heating | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialAncillary HeatingProgram Development Cost | WA | Residential | Ancillary Heating | Program Development Cost | $/program | 0 | Program would piggy-back off of Ancillary-Cooling and share those costs |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialAncillary HeatingProgram Life | WA | Residential | Ancillary Heating | Program Life | years | 10 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialAncillary HeatingProgram Start Year | WA | Residential | Ancillary Heating | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServiceAncillary HeatingSummer DR Event Hours | WA | General Service | Ancillary Heating | Summer DR Event Hours | hours/year | 0 | 0 |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceAncillary HeatingWinter DR Event Hours | WA | General Service | Ancillary Heating | Winter DR Event Hours | hours/year | 36 | 2016 M&V Report Event Hours |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceAncillary HeatingAnnual O&M Cost | WA | General Service | Ancillary Heating | Annual O&M Cost | $/participant/year | 0 | Zero for Ancillary |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceAncillary HeatingAnnual O&M Cost per MW | WA | General Service | Ancillary Heating | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceAncillary HeatingAnnual Program Administration Cost | WA | General Service | Ancillary Heating | Annual Program Administration Cost | $/yr | 0 | Program would piggy-back off of Ancillary-Cooling and share those costs |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceAncillary HeatingCost of Equip + Install | WA | General Service | Ancillary Heating | Cost of Equip + Install | $/tech | 0 | Bring your own thermostat program |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceAncillary HeatingCost of Equip + Install (per kW basis) | WA | General Service | Ancillary Heating | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceAncillary HeatingDe-rate | WA | General Service | Ancillary Heating | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceAncillary HeatingNet to Gross Ratio (free ridership) | WA | General Service | Ancillary Heating | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceAncillary HeatingPer Customer Annual Marketing/Recruitment Cost | WA | General Service | Ancillary Heating | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | Utah $50, All others $60 (25% higher) |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceAncillary HeatingPer Participant Annual Incentive | WA | General Service | Ancillary Heating | Per Participant Annual Incentive | $/participant/year | 20 | Assume $20 per year per system, same as CAC DLC. |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceAncillary HeatingPer kW Annual Incentive | WA | General Service | Ancillary Heating | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceAncillary HeatingProgram Development Cost | WA | General Service | Ancillary Heating | Program Development Cost | $/program | 0 | Program would piggy-back off of Ancillary-Cooling and share those costs |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceAncillary HeatingProgram Life | WA | General Service | Ancillary Heating | Program Life | years | 10 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceAncillary HeatingProgram Start Year | WA | General Service | Ancillary Heating | Program Start Year | year | 2026 | 0 |  | General ServiceProgram Start Year | Market PotentialWA
WAResidentialDLC Water HeatingSummer DR Event Hours | WA | Residential | DLC Water Heating | Summer DR Event Hours | hours/year | 0 | Current PC Cool Keeper CAC DLC program allows for max 100 hours of curtailment. |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialDLC Water HeatingWinter DR Event Hours | WA | Residential | DLC Water Heating | Winter DR Event Hours | hours/year | 0 | Split 50 hrs summer, and 50 hrs winter |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialDLC Water HeatingAnnual O&M Cost | WA | Residential | DLC Water Heating | Annual O&M Cost | $/participant/year | 0 | Assume 5% of equipment + install costs. |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialDLC Water HeatingAnnual O&M Cost per MW | WA | Residential | DLC Water Heating | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialDLC Water HeatingAnnual Program Administration Cost | WA | Residential | DLC Water Heating | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialDLC Water HeatingCost of Equip + Install | WA | Residential | DLC Water Heating | Cost of Equip + Install | $/tech | 0 | Assumed $160 cost for water heater switch (same as cooling switch cost), plus $200 installation cost. Cost of Permit and License is $100 for res and $125 for C&I |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialDLC Water HeatingCost of Equip + Install (per kW basis) | WA | Residential | DLC Water Heating | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialDLC Water HeatingDe-rate | WA | Residential | DLC Water Heating | De-rate | capacity equivalence factor | 0 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialDLC Water HeatingNet to Gross Ratio (free ridership) | WA | Residential | DLC Water Heating | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialDLC Water HeatingPer Customer Annual Marketing/Recruitment Cost | WA | Residential | DLC Water Heating | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as DLC CAC |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialDLC Water HeatingPer Participant Annual Incentive | WA | Residential | DLC Water Heating | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialDLC Water HeatingPer kW Annual Incentive | WA | Residential | DLC Water Heating | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialDLC Water HeatingProgram Development Cost | WA | Residential | DLC Water Heating | Program Development Cost | $/program | 0 | 0 |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialDLC Water HeatingProgram Life | WA | Residential | DLC Water Heating | Program Life | years | 0 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialDLC Water HeatingProgram Start Year | WA | Residential | DLC Water Heating | Program Start Year | year | 0 | Existing programs in UT. Other states need 2 years to ramp up. |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServiceDLC Water HeatingSummer DR Event Hours | WA | General Service | DLC Water Heating | Summer DR Event Hours | hours/year | 0 | Current PC Cool Keeper CAC DLC program allows for max 100 hours of curtailment. |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceDLC Water HeatingWinter DR Event Hours | WA | General Service | DLC Water Heating | Winter DR Event Hours | hours/year | 0 | Split 50 hrs summer, and 50 hrs winter |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceDLC Water HeatingAnnual O&M Cost | WA | General Service | DLC Water Heating | Annual O&M Cost | $/participant/year | 0 | Assume 5% of equipment + install costs. |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceDLC Water HeatingAnnual O&M Cost per MW | WA | General Service | DLC Water Heating | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceDLC Water HeatingAnnual Program Administration Cost | WA | General Service | DLC Water Heating | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceDLC Water HeatingCost of Equip + Install | WA | General Service | DLC Water Heating | Cost of Equip + Install | $/tech | 0 | Assumed $160 cost for water heater switch (same as cooling switch cost), plus $200 installation cost. Cost of Permit and License is $100 for res and $125 for C&I |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceDLC Water HeatingCost of Equip + Install (per kW basis) | WA | General Service | DLC Water Heating | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceDLC Water HeatingDe-rate | WA | General Service | DLC Water Heating | De-rate | capacity equivalence factor | 0 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceDLC Water HeatingNet to Gross Ratio (free ridership) | WA | General Service | DLC Water Heating | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceDLC Water HeatingPer Customer Annual Marketing/Recruitment Cost | WA | General Service | DLC Water Heating | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as DLC CAC |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceDLC Water HeatingPer Participant Annual Incentive | WA | General Service | DLC Water Heating | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceDLC Water HeatingPer kW Annual Incentive | WA | General Service | DLC Water Heating | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceDLC Water HeatingProgram Development Cost | WA | General Service | DLC Water Heating | Program Development Cost | $/program | 0 | No startup costs; Framework already exists for current programs |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceDLC Water HeatingProgram Life | WA | General Service | DLC Water Heating | Program Life | years | 0 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceDLC Water HeatingProgram Start Year | WA | General Service | DLC Water Heating | Program Start Year | year | 0 | Existing programs in UT. Other states need 2 years to ramp up. |  | General ServiceProgram Start Year | Market PotentialWA
WAResidentialAncillary DLC WHSummer DR Event Hours | WA | Residential | Ancillary DLC WH | Summer DR Event Hours | hours/year | 0 | Current PC Cool Keeper CAC DLC program allows for max 100 hours of curtailment. |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialAncillary DLC WHWinter DR Event Hours | WA | Residential | Ancillary DLC WH | Winter DR Event Hours | hours/year | 0 | Split 50 hrs summer, and 50 hrs winter |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialAncillary DLC WHAnnual O&M Cost | WA | Residential | Ancillary DLC WH | Annual O&M Cost | $/participant/year | 0 | Zero for Ancillary |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialAncillary DLC WHAnnual O&M Cost per MW | WA | Residential | Ancillary DLC WH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialAncillary DLC WHAnnual Program Administration Cost | WA | Residential | Ancillary DLC WH | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialAncillary DLC WHCost of Equip + Install | WA | Residential | Ancillary DLC WH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialAncillary DLC WHCost of Equip + Install (per kW basis) | WA | Residential | Ancillary DLC WH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialAncillary DLC WHDe-rate | WA | Residential | Ancillary DLC WH | De-rate | capacity equivalence factor | 0 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialAncillary DLC WHNet to Gross Ratio (free ridership) | WA | Residential | Ancillary DLC WH | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialAncillary DLC WHPer Customer Annual Marketing/Recruitment Cost | WA | Residential | Ancillary DLC WH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as DLC CAC |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialAncillary DLC WHPer Participant Annual Incentive | WA | Residential | Ancillary DLC WH | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialAncillary DLC WHPer kW Annual Incentive | WA | Residential | Ancillary DLC WH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialAncillary DLC WHProgram Development Cost | WA | Residential | Ancillary DLC WH | Program Development Cost | $/program | 0 | 0 |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialAncillary DLC WHProgram Life | WA | Residential | Ancillary DLC WH | Program Life | years | 0 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialAncillary DLC WHProgram Start Year | WA | Residential | Ancillary DLC WH | Program Start Year | year | 0 | Existing programs in UT. Other states need 2 years to ramp up. |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServiceAncillary DLC WHSummer DR Event Hours | WA | General Service | Ancillary DLC WH | Summer DR Event Hours | hours/year | 0 | Current PC Cool Keeper CAC DLC program allows for max 100 hours of curtailment. |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceAncillary DLC WHWinter DR Event Hours | WA | General Service | Ancillary DLC WH | Winter DR Event Hours | hours/year | 0 | Split 50 hrs summer, and 50 hrs winter |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceAncillary DLC WHAnnual O&M Cost | WA | General Service | Ancillary DLC WH | Annual O&M Cost | $/participant/year | 0 | Zero for Ancillary |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceAncillary DLC WHAnnual O&M Cost per MW | WA | General Service | Ancillary DLC WH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceAncillary DLC WHAnnual Program Administration Cost | WA | General Service | Ancillary DLC WH | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceAncillary DLC WHCost of Equip + Install | WA | General Service | Ancillary DLC WH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceAncillary DLC WHCost of Equip + Install (per kW basis) | WA | General Service | Ancillary DLC WH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceAncillary DLC WHDe-rate | WA | General Service | Ancillary DLC WH | De-rate | capacity equivalence factor | 0 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceAncillary DLC WHNet to Gross Ratio (free ridership) | WA | General Service | Ancillary DLC WH | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceAncillary DLC WHPer Customer Annual Marketing/Recruitment Cost | WA | General Service | Ancillary DLC WH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as DLC CAC |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceAncillary DLC WHPer Participant Annual Incentive | WA | General Service | Ancillary DLC WH | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceAncillary DLC WHPer kW Annual Incentive | WA | General Service | Ancillary DLC WH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceAncillary DLC WHProgram Development Cost | WA | General Service | Ancillary DLC WH | Program Development Cost | $/program | 0 | No startup costs; Framework already exists for current programs |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceAncillary DLC WHProgram Life | WA | General Service | Ancillary DLC WH | Program Life | years | 0 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceAncillary DLC WHProgram Start Year | WA | General Service | Ancillary DLC WH | Program Start Year | year | 0 | Existing programs in UT. Other states need 2 years to ramp up. |  | General ServiceProgram Start Year | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHSummer DR Event Hours | WA | Residential | Pilot-CTA-2045 HPWH | Summer DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHWinter DR Event Hours | WA | Residential | Pilot-CTA-2045 HPWH | Winter DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHAnnual O&M Cost | WA | Residential | Pilot-CTA-2045 HPWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHAnnual O&M Cost per MW | WA | Residential | Pilot-CTA-2045 HPWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHAnnual Program Administration Cost | WA | Residential | Pilot-CTA-2045 HPWH | Annual Program Administration Cost | $/yr | 9479.6328 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHCost of Equip + Install | WA | Residential | Pilot-CTA-2045 HPWH | Cost of Equip + Install | $/tech | 170 | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 for these customers)- average customer will be $170 |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHCost of Equip + Install (per kW basis) | WA | Residential | Pilot-CTA-2045 HPWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHDe-rate | WA | Residential | Pilot-CTA-2045 HPWH | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHNet to Gross Ratio (free ridership) | WA | Residential | Pilot-CTA-2045 HPWH | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHPer Customer Annual Marketing/Recruitment Cost | WA | Residential | Pilot-CTA-2045 HPWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Same as Smart Thermostats |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHPer Participant Annual Incentive | WA | Residential | Pilot-CTA-2045 HPWH | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHPer kW Annual Incentive | WA | Residential | Pilot-CTA-2045 HPWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHProgram Development Cost | WA | Residential | Pilot-CTA-2045 HPWH | Program Development Cost | $/program | 7899.694 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHProgram Life | WA | Residential | Pilot-CTA-2045 HPWH | Program Life | years | 8 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialPilot-CTA-2045 HPWHProgram Start Year | WA | Residential | Pilot-CTA-2045 HPWH | Program Start Year | year | 2024 | 0 |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHSummer DR Event Hours | WA | General Service | Pilot-CTA-2045 HPWH | Summer DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHWinter DR Event Hours | WA | General Service | Pilot-CTA-2045 HPWH | Winter DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHAnnual O&M Cost | WA | General Service | Pilot-CTA-2045 HPWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHAnnual O&M Cost per MW | WA | General Service | Pilot-CTA-2045 HPWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHAnnual Program Administration Cost | WA | General Service | Pilot-CTA-2045 HPWH | Annual Program Administration Cost | $/yr | 35520.3672 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHCost of Equip + Install | WA | General Service | Pilot-CTA-2045 HPWH | Cost of Equip + Install | $/tech | 170 | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 install cost for these customers)- average customer will be $170 |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHCost of Equip + Install (per kW basis) | WA | General Service | Pilot-CTA-2045 HPWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHDe-rate | WA | General Service | Pilot-CTA-2045 HPWH | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHNet to Gross Ratio (free ridership) | WA | General Service | Pilot-CTA-2045 HPWH | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHPer Customer Annual Marketing/Recruitment Cost | WA | General Service | Pilot-CTA-2045 HPWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | Same as Smart Thermostats |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHPer Participant Annual Incentive | WA | General Service | Pilot-CTA-2045 HPWH | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHPer kW Annual Incentive | WA | General Service | Pilot-CTA-2045 HPWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHProgram Development Cost | WA | General Service | Pilot-CTA-2045 HPWH | Program Development Cost | $/program | 29600.306 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHProgram Life | WA | General Service | Pilot-CTA-2045 HPWH | Program Life | years | 8 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 HPWHProgram Start Year | WA | General Service | Pilot-CTA-2045 HPWH | Program Start Year | year | 2024 | 0 |  | General ServiceProgram Start Year | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHSummer DR Event Hours | WA | Residential | Parent-CTA-2045 HPWH | Summer DR Event Hours | hours/year | 210 | 2024 Avista Update: 70 events each season, 3 hours each |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHWinter DR Event Hours | WA | Residential | Parent-CTA-2045 HPWH | Winter DR Event Hours | hours/year | 210 | 2024 Avista Update: 70 events each season, 3 hours each |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHAnnual O&M Cost | WA | Residential | Parent-CTA-2045 HPWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHAnnual O&M Cost per MW | WA | Residential | Parent-CTA-2045 HPWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHAnnual Program Administration Cost | WA | Residential | Parent-CTA-2045 HPWH | Annual Program Administration Cost | $/yr | 9479.6328 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHCost of Equip + Install | WA | Residential | Parent-CTA-2045 HPWH | Cost of Equip + Install | $/tech | 170 | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 for these customers)- average customer will be $170 |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHCost of Equip + Install (per kW basis) | WA | Residential | Parent-CTA-2045 HPWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHDe-rate | WA | Residential | Parent-CTA-2045 HPWH | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHNet to Gross Ratio (free ridership) | WA | Residential | Parent-CTA-2045 HPWH | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHPer Customer Annual Marketing/Recruitment Cost | WA | Residential | Parent-CTA-2045 HPWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Same as Smart Thermostats |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHPer Participant Annual Incentive | WA | Residential | Parent-CTA-2045 HPWH | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHPer kW Annual Incentive | WA | Residential | Parent-CTA-2045 HPWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHProgram Development Cost | WA | Residential | Parent-CTA-2045 HPWH | Program Development Cost | $/program | 7899.694 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHProgram Life | WA | Residential | Parent-CTA-2045 HPWH | Program Life | years | 8 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialParent-CTA-2045 HPWHProgram Start Year | WA | Residential | Parent-CTA-2045 HPWH | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHSummer DR Event Hours | WA | General Service | Parent-CTA-2045 HPWH | Summer DR Event Hours | hours/year | 210 | 2024 Avista Update: 70 events each season, 3 hours each |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHWinter DR Event Hours | WA | General Service | Parent-CTA-2045 HPWH | Winter DR Event Hours | hours/year | 210 | 2024 Avista Update: 70 events each season, 3 hours each |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHAnnual O&M Cost | WA | General Service | Parent-CTA-2045 HPWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHAnnual O&M Cost per MW | WA | General Service | Parent-CTA-2045 HPWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHAnnual Program Administration Cost | WA | General Service | Parent-CTA-2045 HPWH | Annual Program Administration Cost | $/yr | 35520.3672 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHCost of Equip + Install | WA | General Service | Parent-CTA-2045 HPWH | Cost of Equip + Install | $/tech | 170 | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 install cost for these customers)- average customer will be $170 |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHCost of Equip + Install (per kW basis) | WA | General Service | Parent-CTA-2045 HPWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHDe-rate | WA | General Service | Parent-CTA-2045 HPWH | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHNet to Gross Ratio (free ridership) | WA | General Service | Parent-CTA-2045 HPWH | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHPer Customer Annual Marketing/Recruitment Cost | WA | General Service | Parent-CTA-2045 HPWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | Same as Smart Thermostats |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHPer Participant Annual Incentive | WA | General Service | Parent-CTA-2045 HPWH | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHPer kW Annual Incentive | WA | General Service | Parent-CTA-2045 HPWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHProgram Development Cost | WA | General Service | Parent-CTA-2045 HPWH | Program Development Cost | $/program | 29600.306 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHProgram Life | WA | General Service | Parent-CTA-2045 HPWH | Program Life | years | 8 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 HPWHProgram Start Year | WA | General Service | Parent-CTA-2045 HPWH | Program Start Year | year | 2026 | 0 |  | General ServiceProgram Start Year | Market PotentialWA
WAResidentialPilot-Ancillary HPWHSummer DR Event Hours | WA | Residential | Pilot-Ancillary HPWH | Summer DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialPilot-Ancillary HPWHWinter DR Event Hours | WA | Residential | Pilot-Ancillary HPWH | Winter DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialPilot-Ancillary HPWHAnnual O&M Cost | WA | Residential | Pilot-Ancillary HPWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialPilot-Ancillary HPWHAnnual O&M Cost per MW | WA | Residential | Pilot-Ancillary HPWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialPilot-Ancillary HPWHAnnual Program Administration Cost | WA | Residential | Pilot-Ancillary HPWH | Annual Program Administration Cost | $/yr |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialPilot-Ancillary HPWHCost of Equip + Install | WA | Residential | Pilot-Ancillary HPWH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialPilot-Ancillary HPWHCost of Equip + Install (per kW basis) | WA | Residential | Pilot-Ancillary HPWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialPilot-Ancillary HPWHDe-rate | WA | Residential | Pilot-Ancillary HPWH | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialPilot-Ancillary HPWHNet to Gross Ratio (free ridership) | WA | Residential | Pilot-Ancillary HPWH | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialPilot-Ancillary HPWHPer Customer Annual Marketing/Recruitment Cost | WA | Residential | Pilot-Ancillary HPWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Same as Smart Thermostats |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialPilot-Ancillary HPWHPer Participant Annual Incentive | WA | Residential | Pilot-Ancillary HPWH | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialPilot-Ancillary HPWHPer kW Annual Incentive | WA | Residential | Pilot-Ancillary HPWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialPilot-Ancillary HPWHProgram Development Cost | WA | Residential | Pilot-Ancillary HPWH | Program Development Cost | $/program |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialPilot-Ancillary HPWHProgram Life | WA | Residential | Pilot-Ancillary HPWH | Program Life | years | 8 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialPilot-Ancillary HPWHProgram Start Year | WA | Residential | Pilot-Ancillary HPWH | Program Start Year | year | 2024 | 0 |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHSummer DR Event Hours | WA | General Service | Pilot-Ancillary HPWH | Summer DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHWinter DR Event Hours | WA | General Service | Pilot-Ancillary HPWH | Winter DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHAnnual O&M Cost | WA | General Service | Pilot-Ancillary HPWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHAnnual O&M Cost per MW | WA | General Service | Pilot-Ancillary HPWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHAnnual Program Administration Cost | WA | General Service | Pilot-Ancillary HPWH | Annual Program Administration Cost | $/yr |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHCost of Equip + Install | WA | General Service | Pilot-Ancillary HPWH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHCost of Equip + Install (per kW basis) | WA | General Service | Pilot-Ancillary HPWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHDe-rate | WA | General Service | Pilot-Ancillary HPWH | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHNet to Gross Ratio (free ridership) | WA | General Service | Pilot-Ancillary HPWH | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHPer Customer Annual Marketing/Recruitment Cost | WA | General Service | Pilot-Ancillary HPWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | Same as Smart Thermostats |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHPer Participant Annual Incentive | WA | General Service | Pilot-Ancillary HPWH | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHPer kW Annual Incentive | WA | General Service | Pilot-Ancillary HPWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHProgram Development Cost | WA | General Service | Pilot-Ancillary HPWH | Program Development Cost | $/program |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHProgram Life | WA | General Service | Pilot-Ancillary HPWH | Program Life | years | 8 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServicePilot-Ancillary HPWHProgram Start Year | WA | General Service | Pilot-Ancillary HPWH | Program Start Year | year | 2024 | 0 |  | General ServiceProgram Start Year | Market PotentialWA
WAResidentialParent-Ancillary HPWHSummer DR Event Hours | WA | Residential | Parent-Ancillary HPWH | Summer DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialParent-Ancillary HPWHWinter DR Event Hours | WA | Residential | Parent-Ancillary HPWH | Winter DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialParent-Ancillary HPWHAnnual O&M Cost | WA | Residential | Parent-Ancillary HPWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialParent-Ancillary HPWHAnnual O&M Cost per MW | WA | Residential | Parent-Ancillary HPWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialParent-Ancillary HPWHAnnual Program Administration Cost | WA | Residential | Parent-Ancillary HPWH | Annual Program Administration Cost | $/yr | 6319.7552 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialParent-Ancillary HPWHCost of Equip + Install | WA | Residential | Parent-Ancillary HPWH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialParent-Ancillary HPWHCost of Equip + Install (per kW basis) | WA | Residential | Parent-Ancillary HPWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialParent-Ancillary HPWHDe-rate | WA | Residential | Parent-Ancillary HPWH | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialParent-Ancillary HPWHNet to Gross Ratio (free ridership) | WA | Residential | Parent-Ancillary HPWH | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialParent-Ancillary HPWHPer Customer Annual Marketing/Recruitment Cost | WA | Residential | Parent-Ancillary HPWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Same as Smart Thermostats |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialParent-Ancillary HPWHPer Participant Annual Incentive | WA | Residential | Parent-Ancillary HPWH | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialParent-Ancillary HPWHPer kW Annual Incentive | WA | Residential | Parent-Ancillary HPWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialParent-Ancillary HPWHProgram Development Cost | WA | Residential | Parent-Ancillary HPWH | Program Development Cost | $/program | 7899.694 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialParent-Ancillary HPWHProgram Life | WA | Residential | Parent-Ancillary HPWH | Program Life | years | 8 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialParent-Ancillary HPWHProgram Start Year | WA | Residential | Parent-Ancillary HPWH | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHSummer DR Event Hours | WA | General Service | Parent-Ancillary HPWH | Summer DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHWinter DR Event Hours | WA | General Service | Parent-Ancillary HPWH | Winter DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHAnnual O&M Cost | WA | General Service | Parent-Ancillary HPWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHAnnual O&M Cost per MW | WA | General Service | Parent-Ancillary HPWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHAnnual Program Administration Cost | WA | General Service | Parent-Ancillary HPWH | Annual Program Administration Cost | $/yr | 23680.2448 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHCost of Equip + Install | WA | General Service | Parent-Ancillary HPWH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHCost of Equip + Install (per kW basis) | WA | General Service | Parent-Ancillary HPWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHDe-rate | WA | General Service | Parent-Ancillary HPWH | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHNet to Gross Ratio (free ridership) | WA | General Service | Parent-Ancillary HPWH | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHPer Customer Annual Marketing/Recruitment Cost | WA | General Service | Parent-Ancillary HPWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | Same as Smart Thermostats |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHPer Participant Annual Incentive | WA | General Service | Parent-Ancillary HPWH | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHPer kW Annual Incentive | WA | General Service | Parent-Ancillary HPWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHProgram Development Cost | WA | General Service | Parent-Ancillary HPWH | Program Development Cost | $/program | 29600.306 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHProgram Life | WA | General Service | Parent-Ancillary HPWH | Program Life | years | 8 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceParent-Ancillary HPWHProgram Start Year | WA | General Service | Parent-Ancillary HPWH | Program Start Year | year | 2026 | 0 |  | General ServiceProgram Start Year | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHSummer DR Event Hours | WA | Residential | Pilot-CTA-2045 ERWH | Summer DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHWinter DR Event Hours | WA | Residential | Pilot-CTA-2045 ERWH | Winter DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHAnnual O&M Cost | WA | Residential | Pilot-CTA-2045 ERWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHAnnual O&M Cost per MW | WA | Residential | Pilot-CTA-2045 ERWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHAnnual Program Administration Cost | WA | Residential | Pilot-CTA-2045 ERWH | Annual Program Administration Cost | $/yr | 40885.047 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHCost of Equip + Install | WA | Residential | Pilot-CTA-2045 ERWH | Cost of Equip + Install | $/tech | 170 | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 for these customers)- average customer will be $170 |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHCost of Equip + Install (per kW basis) | WA | Residential | Pilot-CTA-2045 ERWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHDe-rate | WA | Residential | Pilot-CTA-2045 ERWH | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHNet to Gross Ratio (free ridership) | WA | Residential | Pilot-CTA-2045 ERWH | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHPer Customer Annual Marketing/Recruitment Cost | WA | Residential | Pilot-CTA-2045 ERWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Same as Smart Thermostats |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHPer Participant Annual Incentive | WA | Residential | Pilot-CTA-2045 ERWH | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHPer kW Annual Incentive | WA | Residential | Pilot-CTA-2045 ERWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHProgram Development Cost | WA | Residential | Pilot-CTA-2045 ERWH | Program Development Cost | $/program | 34070.8725 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHProgram Life | WA | Residential | Pilot-CTA-2045 ERWH | Program Life | years | 8 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialPilot-CTA-2045 ERWHProgram Start Year | WA | Residential | Pilot-CTA-2045 ERWH | Program Start Year | year | 2024 | 0 |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHSummer DR Event Hours | WA | General Service | Pilot-CTA-2045 ERWH | Summer DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHWinter DR Event Hours | WA | General Service | Pilot-CTA-2045 ERWH | Winter DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHAnnual O&M Cost | WA | General Service | Pilot-CTA-2045 ERWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHAnnual O&M Cost per MW | WA | General Service | Pilot-CTA-2045 ERWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHAnnual Program Administration Cost | WA | General Service | Pilot-CTA-2045 ERWH | Annual Program Administration Cost | $/yr | 4114.953 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHCost of Equip + Install | WA | General Service | Pilot-CTA-2045 ERWH | Cost of Equip + Install | $/tech | 170 | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 install cost for these customers)- average customer will be $170 |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHCost of Equip + Install (per kW basis) | WA | General Service | Pilot-CTA-2045 ERWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHDe-rate | WA | General Service | Pilot-CTA-2045 ERWH | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHNet to Gross Ratio (free ridership) | WA | General Service | Pilot-CTA-2045 ERWH | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHPer Customer Annual Marketing/Recruitment Cost | WA | General Service | Pilot-CTA-2045 ERWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | Same as Smart Thermostats |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHPer Participant Annual Incentive | WA | General Service | Pilot-CTA-2045 ERWH | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHPer kW Annual Incentive | WA | General Service | Pilot-CTA-2045 ERWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHProgram Development Cost | WA | General Service | Pilot-CTA-2045 ERWH | Program Development Cost | $/program | 3429.1275 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHProgram Life | WA | General Service | Pilot-CTA-2045 ERWH | Program Life | years | 8 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServicePilot-CTA-2045 ERWHProgram Start Year | WA | General Service | Pilot-CTA-2045 ERWH | Program Start Year | year | 2024 | 0 |  | General ServiceProgram Start Year | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHSummer DR Event Hours | WA | Residential | Parent-CTA-2045 ERWH | Summer DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHWinter DR Event Hours | WA | Residential | Parent-CTA-2045 ERWH | Winter DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHAnnual O&M Cost | WA | Residential | Parent-CTA-2045 ERWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHAnnual O&M Cost per MW | WA | Residential | Parent-CTA-2045 ERWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHAnnual Program Administration Cost | WA | Residential | Parent-CTA-2045 ERWH | Annual Program Administration Cost | $/yr | 40885.047 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHCost of Equip + Install | WA | Residential | Parent-CTA-2045 ERWH | Cost of Equip + Install | $/tech | 170 | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 for these customers)- average customer will be $170 |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHCost of Equip + Install (per kW basis) | WA | Residential | Parent-CTA-2045 ERWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHDe-rate | WA | Residential | Parent-CTA-2045 ERWH | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHNet to Gross Ratio (free ridership) | WA | Residential | Parent-CTA-2045 ERWH | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHPer Customer Annual Marketing/Recruitment Cost | WA | Residential | Parent-CTA-2045 ERWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Same as Smart Thermostats |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHPer Participant Annual Incentive | WA | Residential | Parent-CTA-2045 ERWH | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHPer kW Annual Incentive | WA | Residential | Parent-CTA-2045 ERWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHProgram Development Cost | WA | Residential | Parent-CTA-2045 ERWH | Program Development Cost | $/program | 34070.8725 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHProgram Life | WA | Residential | Parent-CTA-2045 ERWH | Program Life | years | 8 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialParent-CTA-2045 ERWHProgram Start Year | WA | Residential | Parent-CTA-2045 ERWH | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHSummer DR Event Hours | WA | General Service | Parent-CTA-2045 ERWH | Summer DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHWinter DR Event Hours | WA | General Service | Parent-CTA-2045 ERWH | Winter DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHAnnual O&M Cost | WA | General Service | Parent-CTA-2045 ERWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHAnnual O&M Cost per MW | WA | General Service | Parent-CTA-2045 ERWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHAnnual Program Administration Cost | WA | General Service | Parent-CTA-2045 ERWH | Annual Program Administration Cost | $/yr | 4114.953 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHCost of Equip + Install | WA | General Service | Parent-CTA-2045 ERWH | Cost of Equip + Install | $/tech | 170 | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 install cost for these customers)- average customer will be $170 |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHCost of Equip + Install (per kW basis) | WA | General Service | Parent-CTA-2045 ERWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHDe-rate | WA | General Service | Parent-CTA-2045 ERWH | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHNet to Gross Ratio (free ridership) | WA | General Service | Parent-CTA-2045 ERWH | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHPer Customer Annual Marketing/Recruitment Cost | WA | General Service | Parent-CTA-2045 ERWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | Same as Smart Thermostats |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHPer Participant Annual Incentive | WA | General Service | Parent-CTA-2045 ERWH | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHPer kW Annual Incentive | WA | General Service | Parent-CTA-2045 ERWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHProgram Development Cost | WA | General Service | Parent-CTA-2045 ERWH | Program Development Cost | $/program | 3429.1275 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHProgram Life | WA | General Service | Parent-CTA-2045 ERWH | Program Life | years | 8 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceParent-CTA-2045 ERWHProgram Start Year | WA | General Service | Parent-CTA-2045 ERWH | Program Start Year | year | 2026 | 0 |  | General ServiceProgram Start Year | Market PotentialWA
WAResidentialPilot-Ancillary ERWHSummer DR Event Hours | WA | Residential | Pilot-Ancillary ERWH | Summer DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialPilot-Ancillary ERWHWinter DR Event Hours | WA | Residential | Pilot-Ancillary ERWH | Winter DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialPilot-Ancillary ERWHAnnual O&M Cost | WA | Residential | Pilot-Ancillary ERWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialPilot-Ancillary ERWHAnnual O&M Cost per MW | WA | Residential | Pilot-Ancillary ERWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialPilot-Ancillary ERWHAnnual Program Administration Cost | WA | Residential | Pilot-Ancillary ERWH | Annual Program Administration Cost | $/yr |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialPilot-Ancillary ERWHCost of Equip + Install | WA | Residential | Pilot-Ancillary ERWH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialPilot-Ancillary ERWHCost of Equip + Install (per kW basis) | WA | Residential | Pilot-Ancillary ERWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialPilot-Ancillary ERWHDe-rate | WA | Residential | Pilot-Ancillary ERWH | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialPilot-Ancillary ERWHNet to Gross Ratio (free ridership) | WA | Residential | Pilot-Ancillary ERWH | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialPilot-Ancillary ERWHPer Customer Annual Marketing/Recruitment Cost | WA | Residential | Pilot-Ancillary ERWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Same as Smart Thermostats |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialPilot-Ancillary ERWHPer Participant Annual Incentive | WA | Residential | Pilot-Ancillary ERWH | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialPilot-Ancillary ERWHPer kW Annual Incentive | WA | Residential | Pilot-Ancillary ERWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialPilot-Ancillary ERWHProgram Development Cost | WA | Residential | Pilot-Ancillary ERWH | Program Development Cost | $/program |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialPilot-Ancillary ERWHProgram Life | WA | Residential | Pilot-Ancillary ERWH | Program Life | years | 8 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialPilot-Ancillary ERWHProgram Start Year | WA | Residential | Pilot-Ancillary ERWH | Program Start Year | year | 2024 | 0 |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHSummer DR Event Hours | WA | General Service | Pilot-Ancillary ERWH | Summer DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHWinter DR Event Hours | WA | General Service | Pilot-Ancillary ERWH | Winter DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHAnnual O&M Cost | WA | General Service | Pilot-Ancillary ERWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHAnnual O&M Cost per MW | WA | General Service | Pilot-Ancillary ERWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHAnnual Program Administration Cost | WA | General Service | Pilot-Ancillary ERWH | Annual Program Administration Cost | $/yr |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHCost of Equip + Install | WA | General Service | Pilot-Ancillary ERWH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHCost of Equip + Install (per kW basis) | WA | General Service | Pilot-Ancillary ERWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHDe-rate | WA | General Service | Pilot-Ancillary ERWH | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHNet to Gross Ratio (free ridership) | WA | General Service | Pilot-Ancillary ERWH | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHPer Customer Annual Marketing/Recruitment Cost | WA | General Service | Pilot-Ancillary ERWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | Same as Smart Thermostats |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHPer Participant Annual Incentive | WA | General Service | Pilot-Ancillary ERWH | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHPer kW Annual Incentive | WA | General Service | Pilot-Ancillary ERWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHProgram Development Cost | WA | General Service | Pilot-Ancillary ERWH | Program Development Cost | $/program |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHProgram Life | WA | General Service | Pilot-Ancillary ERWH | Program Life | years | 8 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServicePilot-Ancillary ERWHProgram Start Year | WA | General Service | Pilot-Ancillary ERWH | Program Start Year | year | 2024 | 0 |  | General ServiceProgram Start Year | Market PotentialWA
WAResidentialParent-Ancillary ERWHSummer DR Event Hours | WA | Residential | Parent-Ancillary ERWH | Summer DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialParent-Ancillary ERWHWinter DR Event Hours | WA | Residential | Parent-Ancillary ERWH | Winter DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialParent-Ancillary ERWHAnnual O&M Cost | WA | Residential | Parent-Ancillary ERWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialParent-Ancillary ERWHAnnual O&M Cost per MW | WA | Residential | Parent-Ancillary ERWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialParent-Ancillary ERWHAnnual Program Administration Cost | WA | Residential | Parent-Ancillary ERWH | Annual Program Administration Cost | $/yr | 27256.698 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialParent-Ancillary ERWHCost of Equip + Install | WA | Residential | Parent-Ancillary ERWH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialParent-Ancillary ERWHCost of Equip + Install (per kW basis) | WA | Residential | Parent-Ancillary ERWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialParent-Ancillary ERWHDe-rate | WA | Residential | Parent-Ancillary ERWH | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialParent-Ancillary ERWHNet to Gross Ratio (free ridership) | WA | Residential | Parent-Ancillary ERWH | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialParent-Ancillary ERWHPer Customer Annual Marketing/Recruitment Cost | WA | Residential | Parent-Ancillary ERWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Same as Smart Thermostats |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialParent-Ancillary ERWHPer Participant Annual Incentive | WA | Residential | Parent-Ancillary ERWH | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialParent-Ancillary ERWHPer kW Annual Incentive | WA | Residential | Parent-Ancillary ERWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialParent-Ancillary ERWHProgram Development Cost | WA | Residential | Parent-Ancillary ERWH | Program Development Cost | $/program | 34070.8725 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialParent-Ancillary ERWHProgram Life | WA | Residential | Parent-Ancillary ERWH | Program Life | years | 8 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialParent-Ancillary ERWHProgram Start Year | WA | Residential | Parent-Ancillary ERWH | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHSummer DR Event Hours | WA | General Service | Parent-Ancillary ERWH | Summer DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHWinter DR Event Hours | WA | General Service | Parent-Ancillary ERWH | Winter DR Event Hours | hours/year | 75 | 25 total events around 3 hrs ea. |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHAnnual O&M Cost | WA | General Service | Parent-Ancillary ERWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHAnnual O&M Cost per MW | WA | General Service | Parent-Ancillary ERWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHAnnual Program Administration Cost | WA | General Service | Parent-Ancillary ERWH | Annual Program Administration Cost | $/yr | 2743.302 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHCost of Equip + Install | WA | General Service | Parent-Ancillary ERWH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHCost of Equip + Install (per kW basis) | WA | General Service | Parent-Ancillary ERWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHDe-rate | WA | General Service | Parent-Ancillary ERWH | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHNet to Gross Ratio (free ridership) | WA | General Service | Parent-Ancillary ERWH | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHPer Customer Annual Marketing/Recruitment Cost | WA | General Service | Parent-Ancillary ERWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | Same as Smart Thermostats |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHPer Participant Annual Incentive | WA | General Service | Parent-Ancillary ERWH | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHPer kW Annual Incentive | WA | General Service | Parent-Ancillary ERWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHProgram Development Cost | WA | General Service | Parent-Ancillary ERWH | Program Development Cost | $/program | 3429.1275 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHProgram Life | WA | General Service | Parent-Ancillary ERWH | Program Life | years | 8 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceParent-Ancillary ERWHProgram Start Year | WA | General Service | Parent-Ancillary ERWH | Program Start Year | year | 2026 | 0 |  | General ServiceProgram Start Year | Market PotentialWA
WAResidentialDLC Smart AppliancesSummer DR Event Hours | WA | Residential | DLC Smart Appliances | Summer DR Event Hours | hours/year | 528 | Pacificorp: Six hours on-peak period each summer weekday |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialDLC Smart AppliancesWinter DR Event Hours | WA | Residential | DLC Smart Appliances | Winter DR Event Hours | hours/year | 528 | Pacificorp: Six hours on-peak period each winter weekday |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialDLC Smart AppliancesAnnual O&M Cost | WA | Residential | DLC Smart Appliances | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialDLC Smart AppliancesAnnual O&M Cost per MW | WA | Residential | DLC Smart Appliances | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialDLC Smart AppliancesAnnual Program Administration Cost | WA | Residential | DLC Smart Appliances | Annual Program Administration Cost | $/yr | 52289.634 | Share of Cost as noted in table at right |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialDLC Smart AppliancesCost of Equip + Install | WA | Residential | DLC Smart Appliances | Cost of Equip + Install | $/tech | 300 | Google research revealed devices range anywhere between $150 -400. Need wifi hub or some sort to connect devices. See email between Dave & Victoria 5-9-16 |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialDLC Smart AppliancesCost of Equip + Install (per kW basis) | WA | Residential | DLC Smart Appliances | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialDLC Smart AppliancesDe-rate | WA | Residential | DLC Smart Appliances | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialDLC Smart AppliancesNet to Gross Ratio (free ridership) | WA | Residential | DLC Smart Appliances | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialDLC Smart AppliancesPer Customer Annual Marketing/Recruitment Cost | WA | Residential | DLC Smart Appliances | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | 0 |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialDLC Smart AppliancesPer Participant Annual Incentive | WA | Residential | DLC Smart Appliances | Per Participant Annual Incentive | $/participant/year | 0 | 0 |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialDLC Smart AppliancesPer kW Annual Incentive | WA | Residential | DLC Smart Appliances | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialDLC Smart AppliancesProgram Development Cost | WA | Residential | DLC Smart Appliances | Program Development Cost | $/program | 43574.695 | Share of Cost as noted in table at right |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialDLC Smart AppliancesProgram Life | WA | Residential | DLC Smart Appliances | Program Life | years | 8 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialDLC Smart AppliancesProgram Start Year | WA | Residential | DLC Smart Appliances | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesSummer DR Event Hours | WA | General Service | DLC Smart Appliances | Summer DR Event Hours | hours/year | 528 | Pacificorp: Six hours on-peak period each summer weekday |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesWinter DR Event Hours | WA | General Service | DLC Smart Appliances | Winter DR Event Hours | hours/year | 528 | Pacificorp: Six hours on-peak period each winter weekday |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesAnnual O&M Cost | WA | General Service | DLC Smart Appliances | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesAnnual O&M Cost per MW | WA | General Service | DLC Smart Appliances | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesAnnual Program Administration Cost | WA | General Service | DLC Smart Appliances | Annual Program Administration Cost | $/yr | 5266.3286 | Share of Cost as noted in table at right |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesCost of Equip + Install | WA | General Service | DLC Smart Appliances | Cost of Equip + Install | $/tech | 300 | Google research revealed devices range anywhere between $150 -400. Need wifi hub or some sort to connect devices. See email between Dave & Victoria 5-9-16 |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesCost of Equip + Install (per kW basis) | WA | General Service | DLC Smart Appliances | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesDe-rate | WA | General Service | DLC Smart Appliances | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesNet to Gross Ratio (free ridership) | WA | General Service | DLC Smart Appliances | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesPer Customer Annual Marketing/Recruitment Cost | WA | General Service | DLC Smart Appliances | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | 0 |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesPer Participant Annual Incentive | WA | General Service | DLC Smart Appliances | Per Participant Annual Incentive | $/participant/year | 0 | 0 |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesPer kW Annual Incentive | WA | General Service | DLC Smart Appliances | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesProgram Development Cost | WA | General Service | DLC Smart Appliances | Program Development Cost | $/program | 4388.6072 | Share of Cost as noted in table at right |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesProgram Life | WA | General Service | DLC Smart Appliances | Program Life | years | 8 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceDLC Smart AppliancesProgram Start Year | WA | General Service | DLC Smart Appliances | Program Start Year | year | 2026 | 0 |  | General ServiceProgram Start Year | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingSummer DR Event Hours | WA | Res-EV | DLC Electric Vehicle Charging | Summer DR Event Hours | hours/year | 528 | Pacificorp: Six hours on-peak period each summer weekday |  | Res-EVSummer DR Event Hours | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingWinter DR Event Hours | WA | Res-EV | DLC Electric Vehicle Charging | Winter DR Event Hours | hours/year | 528 | Pacificorp: Six hours on-peak period each winter weekday |  | Res-EVWinter DR Event Hours | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingAnnual O&M Cost | WA | Res-EV | DLC Electric Vehicle Charging | Annual O&M Cost | $/participant/year | 45 | 2024 Avista Update: $45 per car (300 cars minimum) |  | Res-EVAnnual O&M Cost | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingAnnual O&M Cost per MW | WA | Res-EV | DLC Electric Vehicle Charging | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | Res-EVAnnual O&M Cost per MW | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingAnnual Program Administration Cost | WA | Res-EV | DLC Electric Vehicle Charging | Annual Program Administration Cost | $/yr | 80000 | 2024 Avista Update: Share of Cost as noted in table at right |  | Res-EVAnnual Program Administration Cost | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingCost of Equip + Install | WA | Res-EV | DLC Electric Vehicle Charging | Cost of Equip + Install | $/tech | 500 | 10/26: $1766 from Avista 2019 EVSE report. Instead of covering cost fo equipment, Avista wants to model offering a partial incentive. Benchmarked $500 based on WA rebates. OLD: Updated cost of equipment and install to $700 per Avista email on 8/25/2020 |  | Res-EVCost of Equip + Install | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingCost of Equip + Install (per kW basis) | WA | Res-EV | DLC Electric Vehicle Charging | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | Res-EVCost of Equip + Install (per kW basis) | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingDe-rate | WA | Res-EV | DLC Electric Vehicle Charging | De-rate | capacity equivalence factor | 1 | 0 |  | Res-EVDe-rate | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingNet to Gross Ratio (free ridership) | WA | Res-EV | DLC Electric Vehicle Charging | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | Res-EVNet to Gross Ratio (free ridership) | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingPer Customer Annual Marketing/Recruitment Cost | WA | Res-EV | DLC Electric Vehicle Charging | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 350 | 2024 Avista Update |  | Res-EVPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingPer Participant Annual Incentive | WA | Res-EV | DLC Electric Vehicle Charging | Per Participant Annual Incentive | $/participant/year | 60 | 2024 Avista Update: $5/month for 1st year; $0 if cust charges 3+ times on peak |  | Res-EVPer Participant Annual Incentive | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingPer kW Annual Incentive | WA | Res-EV | DLC Electric Vehicle Charging | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | Res-EVPer kW Annual Incentive | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingProgram Development Cost | WA | Res-EV | DLC Electric Vehicle Charging | Program Development Cost | $/program | 200000 | Share of Cost as noted in table at right |  | Res-EVProgram Development Cost | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingProgram Life | WA | Res-EV | DLC Electric Vehicle Charging | Program Life | years | 8 | 0 |  | Res-EVProgram Life | Market PotentialWA
WARes-EVDLC Electric Vehicle ChargingProgram Start Year | WA | Res-EV | DLC Electric Vehicle Charging | Program Start Year | year | 2025 | 2024 Avista Update |  | Res-EVProgram Start Year | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingSummer DR Event Hours | WA | GS-EV | DLC Electric Vehicle Charging | Summer DR Event Hours | hours/year |  |  |  | GS-EVSummer DR Event Hours | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingWinter DR Event Hours | WA | GS-EV | DLC Electric Vehicle Charging | Winter DR Event Hours | hours/year |  |  |  | GS-EVWinter DR Event Hours | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingAnnual O&M Cost | WA | GS-EV | DLC Electric Vehicle Charging | Annual O&M Cost | $/participant/year |  |  |  | GS-EVAnnual O&M Cost | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingAnnual O&M Cost per MW | WA | GS-EV | DLC Electric Vehicle Charging | Annual O&M Cost per MW | $/MW @meter |  |  |  | GS-EVAnnual O&M Cost per MW | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingAnnual Program Administration Cost | WA | GS-EV | DLC Electric Vehicle Charging | Annual Program Administration Cost | $/yr |  |  |  | GS-EVAnnual Program Administration Cost | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingCost of Equip + Install | WA | GS-EV | DLC Electric Vehicle Charging | Cost of Equip + Install | $/tech |  |  |  | GS-EVCost of Equip + Install | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingCost of Equip + Install (per kW basis) | WA | GS-EV | DLC Electric Vehicle Charging | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | GS-EVCost of Equip + Install (per kW basis) | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingDe-rate | WA | GS-EV | DLC Electric Vehicle Charging | De-rate | capacity equivalence factor |  |  |  | GS-EVDe-rate | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingNet to Gross Ratio (free ridership) | WA | GS-EV | DLC Electric Vehicle Charging | Net to Gross Ratio (free ridership) | ratio |  |  |  | GS-EVNet to Gross Ratio (free ridership) | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingPer Customer Annual Marketing/Recruitment Cost | WA | GS-EV | DLC Electric Vehicle Charging | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | GS-EVPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingPer Participant Annual Incentive | WA | GS-EV | DLC Electric Vehicle Charging | Per Participant Annual Incentive | $/participant/year |  |  |  | GS-EVPer Participant Annual Incentive | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingPer kW Annual Incentive | WA | GS-EV | DLC Electric Vehicle Charging | Per kW Annual Incentive | $/kW @meter/year |  |  |  | GS-EVPer kW Annual Incentive | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingProgram Development Cost | WA | GS-EV | DLC Electric Vehicle Charging | Program Development Cost | $/program |  |  |  | GS-EVProgram Development Cost | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingProgram Life | WA | GS-EV | DLC Electric Vehicle Charging | Program Life | years |  |  |  | GS-EVProgram Life | Market PotentialWA
WAGS-EVDLC Electric Vehicle ChargingProgram Start Year | WA | GS-EV | DLC Electric Vehicle Charging | Program Start Year | year |  |  |  | GS-EVProgram Start Year | Market PotentialWA
WARes-EVAncillary EVSummer DR Event Hours | WA | Res-EV | Ancillary EV | Summer DR Event Hours | hours/year | 528 | Pacificorp: Six hours on-peak period each summer weekday |  | Res-EVSummer DR Event Hours | Market PotentialWA
WARes-EVAncillary EVWinter DR Event Hours | WA | Res-EV | Ancillary EV | Winter DR Event Hours | hours/year | 528 | Pacificorp: Six hours on-peak period each winter weekday |  | Res-EVWinter DR Event Hours | Market PotentialWA
WARes-EVAncillary EVAnnual O&M Cost | WA | Res-EV | Ancillary EV | Annual O&M Cost | $/participant/year | 0 | Zero for Ancillary |  | Res-EVAnnual O&M Cost | Market PotentialWA
WARes-EVAncillary EVAnnual O&M Cost per MW | WA | Res-EV | Ancillary EV | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | Res-EVAnnual O&M Cost per MW | Market PotentialWA
WARes-EVAncillary EVAnnual Program Administration Cost | WA | Res-EV | Ancillary EV | Annual Program Administration Cost | $/yr | 25786.8986 | Share of Cost as noted in table at right |  | Res-EVAnnual Program Administration Cost | Market PotentialWA
WARes-EVAncillary EVCost of Equip + Install | WA | Res-EV | Ancillary EV | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | Res-EVCost of Equip + Install | Market PotentialWA
WARes-EVAncillary EVCost of Equip + Install (per kW basis) | WA | Res-EV | Ancillary EV | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | Res-EVCost of Equip + Install (per kW basis) | Market PotentialWA
WARes-EVAncillary EVDe-rate | WA | Res-EV | Ancillary EV | De-rate | capacity equivalence factor | 1 | 0 |  | Res-EVDe-rate | Market PotentialWA
WARes-EVAncillary EVNet to Gross Ratio (free ridership) | WA | Res-EV | Ancillary EV | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | Res-EVNet to Gross Ratio (free ridership) | Market PotentialWA
WARes-EVAncillary EVPer Customer Annual Marketing/Recruitment Cost | WA | Res-EV | Ancillary EV | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | Assumption $50 for RAP C&I, MAP = RAPx1.2 |  | Res-EVPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WARes-EVAncillary EVPer Participant Annual Incentive | WA | Res-EV | Ancillary EV | Per Participant Annual Incentive | $/participant/year | 0 | Avista would provide a rate based charger or give a rebate on it, with no further incentives |  | Res-EVPer Participant Annual Incentive | Market PotentialWA
WARes-EVAncillary EVPer kW Annual Incentive | WA | Res-EV | Ancillary EV | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | Res-EVPer kW Annual Incentive | Market PotentialWA
WARes-EVAncillary EVProgram Development Cost | WA | Res-EV | Ancillary EV | Program Development Cost | $/program | 32233.6232 | Share of Cost as noted in table at right |  | Res-EVProgram Development Cost | Market PotentialWA
WARes-EVAncillary EVProgram Life | WA | Res-EV | Ancillary EV | Program Life | years | 8 | 0 |  | Res-EVProgram Life | Market PotentialWA
WARes-EVAncillary EVProgram Start Year | WA | Res-EV | Ancillary EV | Program Start Year | year | 2025 | 2024 Avista Update |  | Res-EVProgram Start Year | Market PotentialWA
WAGS-EVAncillary EVSummer DR Event Hours | WA | GS-EV | Ancillary EV | Summer DR Event Hours | hours/year | 528 | Pacificorp: Six hours on-peak period each summer weekday |  | GS-EVSummer DR Event Hours | Market PotentialWA
WAGS-EVAncillary EVWinter DR Event Hours | WA | GS-EV | Ancillary EV | Winter DR Event Hours | hours/year | 528 | Pacificorp: Six hours on-peak period each winter weekday |  | GS-EVWinter DR Event Hours | Market PotentialWA
WAGS-EVAncillary EVAnnual O&M Cost | WA | GS-EV | Ancillary EV | Annual O&M Cost | $/participant/year | 0 | Zero for Ancillary |  | GS-EVAnnual O&M Cost | Market PotentialWA
WAGS-EVAncillary EVAnnual O&M Cost per MW | WA | GS-EV | Ancillary EV | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | GS-EVAnnual O&M Cost per MW | Market PotentialWA
WAGS-EVAncillary EVAnnual Program Administration Cost | WA | GS-EV | Ancillary EV | Annual Program Administration Cost | $/yr | 12200.9568 | Share of Cost as noted in table at right |  | GS-EVAnnual Program Administration Cost | Market PotentialWA
WAGS-EVAncillary EVCost of Equip + Install | WA | GS-EV | Ancillary EV | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | GS-EVCost of Equip + Install | Market PotentialWA
WAGS-EVAncillary EVCost of Equip + Install (per kW basis) | WA | GS-EV | Ancillary EV | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | GS-EVCost of Equip + Install (per kW basis) | Market PotentialWA
WAGS-EVAncillary EVDe-rate | WA | GS-EV | Ancillary EV | De-rate | capacity equivalence factor | 1 | 0 |  | GS-EVDe-rate | Market PotentialWA
WAGS-EVAncillary EVNet to Gross Ratio (free ridership) | WA | GS-EV | Ancillary EV | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | GS-EVNet to Gross Ratio (free ridership) | Market PotentialWA
WAGS-EVAncillary EVPer Customer Annual Marketing/Recruitment Cost | WA | GS-EV | Ancillary EV | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 62.5 | 25% higher than residential |  | GS-EVPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGS-EVAncillary EVPer Participant Annual Incentive | WA | GS-EV | Ancillary EV | Per Participant Annual Incentive | $/participant/year | 0 | Avista would provide a rate based charger or give a rebate on it, with no further incentives |  | GS-EVPer Participant Annual Incentive | Market PotentialWA
WAGS-EVAncillary EVPer kW Annual Incentive | WA | GS-EV | Ancillary EV | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | GS-EVPer kW Annual Incentive | Market PotentialWA
WAGS-EVAncillary EVProgram Development Cost | WA | GS-EV | Ancillary EV | Program Development Cost | $/program | 15251.1961 | Share of Cost as noted in table at right |  | GS-EVProgram Development Cost | Market PotentialWA
WAGS-EVAncillary EVProgram Life | WA | GS-EV | Ancillary EV | Program Life | years | 8 | 0 |  | GS-EVProgram Life | Market PotentialWA
WAGS-EVAncillary EVProgram Start Year | WA | GS-EV | Ancillary EV | Program Start Year | year | 2025 | 2024 Avista Update |  | GS-EVProgram Start Year | Market PotentialWA
WAGeneral ServiceThird Party ContractsSummer DR Event Hours | WA | General Service | Third Party Contracts | Summer DR Event Hours | hours/year |  |  |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceThird Party ContractsWinter DR Event Hours | WA | General Service | Third Party Contracts | Winter DR Event Hours | hours/year |  |  |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceThird Party ContractsAnnual O&M Cost | WA | General Service | Third Party Contracts | Annual O&M Cost | $/participant/year |  |  |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceThird Party ContractsAnnual O&M Cost per MW | WA | General Service | Third Party Contracts | Annual O&M Cost per MW | $/MW @meter |  |  |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceThird Party ContractsAnnual Program Administration Cost | WA | General Service | Third Party Contracts | Annual Program Administration Cost | $/yr |  |  |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceThird Party ContractsCost of Equip + Install | WA | General Service | Third Party Contracts | Cost of Equip + Install | $/tech |  |  |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceThird Party ContractsCost of Equip + Install (per kW basis) | WA | General Service | Third Party Contracts | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceThird Party ContractsDe-rate | WA | General Service | Third Party Contracts | De-rate | capacity equivalence factor |  |  |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceThird Party ContractsNet to Gross Ratio (free ridership) | WA | General Service | Third Party Contracts | Net to Gross Ratio (free ridership) | ratio |  |  |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceThird Party ContractsPer Customer Annual Marketing/Recruitment Cost | WA | General Service | Third Party Contracts | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceThird Party ContractsPer Participant Annual Incentive | WA | General Service | Third Party Contracts | Per Participant Annual Incentive | $/participant/year |  |  |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceThird Party ContractsPer kW Annual Incentive | WA | General Service | Third Party Contracts | Per kW Annual Incentive | $/kW @meter/year |  |  |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceThird Party ContractsProgram Development Cost | WA | General Service | Third Party Contracts | Program Development Cost | $/program |  |  |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceThird Party ContractsProgram Life | WA | General Service | Third Party Contracts | Program Life | years |  |  |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceThird Party ContractsProgram Start Year | WA | General Service | Third Party Contracts | Program Start Year | year |  |  |  | General ServiceProgram Start Year | Market PotentialWA
WALarge General ServiceThird Party ContractsSummer DR Event Hours | WA | Large General Service | Third Party Contracts | Summer DR Event Hours | hours/year | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  | Large General ServiceSummer DR Event Hours | Market PotentialWA
WALarge General ServiceThird Party ContractsWinter DR Event Hours | WA | Large General Service | Third Party Contracts | Winter DR Event Hours | hours/year | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  | Large General ServiceWinter DR Event Hours | Market PotentialWA
WALarge General ServiceThird Party ContractsAnnual O&M Cost | WA | Large General Service | Third Party Contracts | Annual O&M Cost | $/participant/year | 0 | included in 3rd Party Program Admin Cost |  | Large General ServiceAnnual O&M Cost | Market PotentialWA
WALarge General ServiceThird Party ContractsAnnual O&M Cost per MW | WA | Large General Service | Third Party Contracts | Annual O&M Cost per MW | $/MW @meter | 80000 | included in 3rd Party Program Admin Cost |  | Large General ServiceAnnual O&M Cost per MW | Market PotentialWA
WALarge General ServiceThird Party ContractsAnnual Program Administration Cost | WA | Large General Service | Third Party Contracts | Annual Program Administration Cost | $/yr | 0 | 0 |  | Large General ServiceAnnual Program Administration Cost | Market PotentialWA
WALarge General ServiceThird Party ContractsCost of Equip + Install | WA | Large General Service | Third Party Contracts | Cost of Equip + Install | $/tech | 0 | included in 3rd Party Program Admin Cost |  | Large General ServiceCost of Equip + Install | Market PotentialWA
WALarge General ServiceThird Party ContractsCost of Equip + Install (per kW basis) | WA | Large General Service | Third Party Contracts | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | included in 3rd Party Program Admin Cost |  | Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WALarge General ServiceThird Party ContractsDe-rate | WA | Large General Service | Third Party Contracts | De-rate | capacity equivalence factor | 1 | 0 |  | Large General ServiceDe-rate | Market PotentialWA
WALarge General ServiceThird Party ContractsNet to Gross Ratio (free ridership) | WA | Large General Service | Third Party Contracts | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WALarge General ServiceThird Party ContractsPer Customer Annual Marketing/Recruitment Cost | WA | Large General Service | Third Party Contracts | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | included in 3rd Party Program Admin Cost |  | Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WALarge General ServiceThird Party ContractsPer Participant Annual Incentive | WA | Large General Service | Third Party Contracts | Per Participant Annual Incentive | $/participant/year | 0 | 0 |  | Large General ServicePer Participant Annual Incentive | Market PotentialWA
WALarge General ServiceThird Party ContractsPer kW Annual Incentive | WA | Large General Service | Third Party Contracts | Per kW Annual Incentive | $/kW @meter/year | 0 | included in 3rd Party Program Admin Cost. Capacity reserve incentive pmt given to customers typically in range of $10 to $70 per kW-year |  | Large General ServicePer kW Annual Incentive | Market PotentialWA
WALarge General ServiceThird Party ContractsProgram Development Cost | WA | Large General Service | Third Party Contracts | Program Development Cost | $/program | 0 | No startup costs; Would be included in 3rd Party Costs |  | Large General ServiceProgram Development Cost | Market PotentialWA
WALarge General ServiceThird Party ContractsProgram Life | WA | Large General Service | Third Party Contracts | Program Life | years | 3 | 0 |  | Large General ServiceProgram Life | Market PotentialWA
WALarge General ServiceThird Party ContractsProgram Start Year | WA | Large General Service | Third Party Contracts | Program Start Year | year | 2026 | 0 |  | Large General ServiceProgram Start Year | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsSummer DR Event Hours | WA | Extra Large General Service | Third Party Contracts | Summer DR Event Hours | hours/year | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  | Extra Large General ServiceSummer DR Event Hours | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsWinter DR Event Hours | WA | Extra Large General Service | Third Party Contracts | Winter DR Event Hours | hours/year | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  | Extra Large General ServiceWinter DR Event Hours | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsAnnual O&M Cost | WA | Extra Large General Service | Third Party Contracts | Annual O&M Cost | $/participant/year | 0 | included in 3rd Party Program Admin Cost |  | Extra Large General ServiceAnnual O&M Cost | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsAnnual O&M Cost per MW | WA | Extra Large General Service | Third Party Contracts | Annual O&M Cost per MW | $/MW @meter | 80000 | included in 3rd Party Program Admin Cost |  | Extra Large General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsAnnual Program Administration Cost | WA | Extra Large General Service | Third Party Contracts | Annual Program Administration Cost | $/yr | 0 | 0 |  | Extra Large General ServiceAnnual Program Administration Cost | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsCost of Equip + Install | WA | Extra Large General Service | Third Party Contracts | Cost of Equip + Install | $/tech | 0 | included in 3rd Party Program Admin Cost |  | Extra Large General ServiceCost of Equip + Install | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsCost of Equip + Install (per kW basis) | WA | Extra Large General Service | Third Party Contracts | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | included in 3rd Party Program Admin Cost |  | Extra Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsDe-rate | WA | Extra Large General Service | Third Party Contracts | De-rate | capacity equivalence factor | 1 | 0 |  | Extra Large General ServiceDe-rate | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsNet to Gross Ratio (free ridership) | WA | Extra Large General Service | Third Party Contracts | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | Extra Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsPer Customer Annual Marketing/Recruitment Cost | WA | Extra Large General Service | Third Party Contracts | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | included in 3rd Party Program Admin Cost |  | Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsPer Participant Annual Incentive | WA | Extra Large General Service | Third Party Contracts | Per Participant Annual Incentive | $/participant/year | 0 | 0 |  | Extra Large General ServicePer Participant Annual Incentive | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsPer kW Annual Incentive | WA | Extra Large General Service | Third Party Contracts | Per kW Annual Incentive | $/kW @meter/year | 0 | included in 3rd Party Program Admin Cost. Capacity reserve incentive pmt given to customers typically in range of $10 to $70 per kW-year |  | Extra Large General ServicePer kW Annual Incentive | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsProgram Development Cost | WA | Extra Large General Service | Third Party Contracts | Program Development Cost | $/program | 0 | No startup costs; Would be included in 3rd Party Costs |  | Extra Large General ServiceProgram Development Cost | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsProgram Life | WA | Extra Large General Service | Third Party Contracts | Program Life | years | 3 | 0 |  | Extra Large General ServiceProgram Life | Market PotentialWA
WAExtra Large General ServiceThird Party ContractsProgram Start Year | WA | Extra Large General Service | Third Party Contracts | Program Start Year | year | 2026 | 0 |  | Extra Large General ServiceProgram Start Year | Market PotentialWA
WAGeneral ServiceAncillary Third PartySummer DR Event Hours | WA | General Service | Ancillary Third Party | Summer DR Event Hours | hours/year |  |  |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceAncillary Third PartyWinter DR Event Hours | WA | General Service | Ancillary Third Party | Winter DR Event Hours | hours/year |  |  |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceAncillary Third PartyAnnual O&M Cost | WA | General Service | Ancillary Third Party | Annual O&M Cost | $/participant/year |  |  |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceAncillary Third PartyAnnual O&M Cost per MW | WA | General Service | Ancillary Third Party | Annual O&M Cost per MW | $/MW @meter |  |  |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceAncillary Third PartyAnnual Program Administration Cost | WA | General Service | Ancillary Third Party | Annual Program Administration Cost | $/yr |  |  |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceAncillary Third PartyCost of Equip + Install | WA | General Service | Ancillary Third Party | Cost of Equip + Install | $/tech |  |  |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceAncillary Third PartyCost of Equip + Install (per kW basis) | WA | General Service | Ancillary Third Party | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceAncillary Third PartyDe-rate | WA | General Service | Ancillary Third Party | De-rate | capacity equivalence factor |  |  |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceAncillary Third PartyNet to Gross Ratio (free ridership) | WA | General Service | Ancillary Third Party | Net to Gross Ratio (free ridership) | ratio |  |  |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceAncillary Third PartyPer Customer Annual Marketing/Recruitment Cost | WA | General Service | Ancillary Third Party | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceAncillary Third PartyPer Participant Annual Incentive | WA | General Service | Ancillary Third Party | Per Participant Annual Incentive | $/participant/year |  |  |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceAncillary Third PartyPer kW Annual Incentive | WA | General Service | Ancillary Third Party | Per kW Annual Incentive | $/kW @meter/year |  |  |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceAncillary Third PartyProgram Development Cost | WA | General Service | Ancillary Third Party | Program Development Cost | $/program |  |  |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceAncillary Third PartyProgram Life | WA | General Service | Ancillary Third Party | Program Life | years |  |  |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceAncillary Third PartyProgram Start Year | WA | General Service | Ancillary Third Party | Program Start Year | year |  |  |  | General ServiceProgram Start Year | Market PotentialWA
WALarge General ServiceAncillary Third PartySummer DR Event Hours | WA | Large General Service | Ancillary Third Party | Summer DR Event Hours | hours/year | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  | Large General ServiceSummer DR Event Hours | Market PotentialWA
WALarge General ServiceAncillary Third PartyWinter DR Event Hours | WA | Large General Service | Ancillary Third Party | Winter DR Event Hours | hours/year | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  | Large General ServiceWinter DR Event Hours | Market PotentialWA
WALarge General ServiceAncillary Third PartyAnnual O&M Cost | WA | Large General Service | Ancillary Third Party | Annual O&M Cost | $/participant/year | 0 | included in 3rd Party Program Admin Cost |  | Large General ServiceAnnual O&M Cost | Market PotentialWA
WALarge General ServiceAncillary Third PartyAnnual O&M Cost per MW | WA | Large General Service | Ancillary Third Party | Annual O&M Cost per MW | $/MW @meter | 40000 | Half for Ancillary |  | Large General ServiceAnnual O&M Cost per MW | Market PotentialWA
WALarge General ServiceAncillary Third PartyAnnual Program Administration Cost | WA | Large General Service | Ancillary Third Party | Annual Program Administration Cost | $/yr | 0 | 0 |  | Large General ServiceAnnual Program Administration Cost | Market PotentialWA
WALarge General ServiceAncillary Third PartyCost of Equip + Install | WA | Large General Service | Ancillary Third Party | Cost of Equip + Install | $/tech | 0 | included in 3rd Party Program Admin Cost |  | Large General ServiceCost of Equip + Install | Market PotentialWA
WALarge General ServiceAncillary Third PartyCost of Equip + Install (per kW basis) | WA | Large General Service | Ancillary Third Party | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | included in 3rd Party Program Admin Cost |  | Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WALarge General ServiceAncillary Third PartyDe-rate | WA | Large General Service | Ancillary Third Party | De-rate | capacity equivalence factor | 1 | 0 |  | Large General ServiceDe-rate | Market PotentialWA
WALarge General ServiceAncillary Third PartyNet to Gross Ratio (free ridership) | WA | Large General Service | Ancillary Third Party | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WALarge General ServiceAncillary Third PartyPer Customer Annual Marketing/Recruitment Cost | WA | Large General Service | Ancillary Third Party | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | included in 3rd Party Program Admin Cost |  | Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WALarge General ServiceAncillary Third PartyPer Participant Annual Incentive | WA | Large General Service | Ancillary Third Party | Per Participant Annual Incentive | $/participant/year | 0 | 0 |  | Large General ServicePer Participant Annual Incentive | Market PotentialWA
WALarge General ServiceAncillary Third PartyPer kW Annual Incentive | WA | Large General Service | Ancillary Third Party | Per kW Annual Incentive | $/kW @meter/year | 0 | included in 3rd Party Program Admin Cost. Capacity reserve incentive pmt given to customers typically in range of $10 to $70 per kW-year |  | Large General ServicePer kW Annual Incentive | Market PotentialWA
WALarge General ServiceAncillary Third PartyProgram Development Cost | WA | Large General Service | Ancillary Third Party | Program Development Cost | $/program | 0 | No startup costs; Would be included in 3rd Party Costs |  | Large General ServiceProgram Development Cost | Market PotentialWA
WALarge General ServiceAncillary Third PartyProgram Life | WA | Large General Service | Ancillary Third Party | Program Life | years | 3 | 0 |  | Large General ServiceProgram Life | Market PotentialWA
WALarge General ServiceAncillary Third PartyProgram Start Year | WA | Large General Service | Ancillary Third Party | Program Start Year | year | 2026 | 0 |  | Large General ServiceProgram Start Year | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartySummer DR Event Hours | WA | Extra Large General Service | Ancillary Third Party | Summer DR Event Hours | hours/year | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  | Extra Large General ServiceSummer DR Event Hours | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartyWinter DR Event Hours | WA | Extra Large General Service | Ancillary Third Party | Winter DR Event Hours | hours/year | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  | Extra Large General ServiceWinter DR Event Hours | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartyAnnual O&M Cost | WA | Extra Large General Service | Ancillary Third Party | Annual O&M Cost | $/participant/year | 0 | included in 3rd Party Program Admin Cost |  | Extra Large General ServiceAnnual O&M Cost | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartyAnnual O&M Cost per MW | WA | Extra Large General Service | Ancillary Third Party | Annual O&M Cost per MW | $/MW @meter | 40000 | Half for Ancillary |  | Extra Large General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartyAnnual Program Administration Cost | WA | Extra Large General Service | Ancillary Third Party | Annual Program Administration Cost | $/yr | 0 | 0 |  | Extra Large General ServiceAnnual Program Administration Cost | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartyCost of Equip + Install | WA | Extra Large General Service | Ancillary Third Party | Cost of Equip + Install | $/tech | 0 | included in 3rd Party Program Admin Cost |  | Extra Large General ServiceCost of Equip + Install | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartyCost of Equip + Install (per kW basis) | WA | Extra Large General Service | Ancillary Third Party | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | included in 3rd Party Program Admin Cost |  | Extra Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartyDe-rate | WA | Extra Large General Service | Ancillary Third Party | De-rate | capacity equivalence factor | 1 | 0 |  | Extra Large General ServiceDe-rate | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartyNet to Gross Ratio (free ridership) | WA | Extra Large General Service | Ancillary Third Party | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | Extra Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartyPer Customer Annual Marketing/Recruitment Cost | WA | Extra Large General Service | Ancillary Third Party | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | included in 3rd Party Program Admin Cost |  | Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartyPer Participant Annual Incentive | WA | Extra Large General Service | Ancillary Third Party | Per Participant Annual Incentive | $/participant/year | 0 | 0 |  | Extra Large General ServicePer Participant Annual Incentive | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartyPer kW Annual Incentive | WA | Extra Large General Service | Ancillary Third Party | Per kW Annual Incentive | $/kW @meter/year | 0 | included in 3rd Party Program Admin Cost. Capacity reserve incentive pmt given to customers typically in range of $10 to $70 per kW-year |  | Extra Large General ServicePer kW Annual Incentive | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartyProgram Development Cost | WA | Extra Large General Service | Ancillary Third Party | Program Development Cost | $/program | 0 | No startup costs; Would be included in 3rd Party Costs |  | Extra Large General ServiceProgram Development Cost | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartyProgram Life | WA | Extra Large General Service | Ancillary Third Party | Program Life | years | 3 | 0 |  | Extra Large General ServiceProgram Life | Market PotentialWA
WAExtra Large General ServiceAncillary Third PartyProgram Start Year | WA | Extra Large General Service | Ancillary Third Party | Program Start Year | year | 2026 | 0 |  | Extra Large General ServiceProgram Start Year | Market PotentialWA
WAGeneral ServiceThermal Energy StorageSummer DR Event Hours | WA | General Service | Thermal Energy Storage | Summer DR Event Hours | hours/year | 36 | Same as TOU, six hours on peak period each summer |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceThermal Energy StorageWinter DR Event Hours | WA | General Service | Thermal Energy Storage | Winter DR Event Hours | hours/year | 0 | 0 |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceThermal Energy StorageAnnual O&M Cost | WA | General Service | Thermal Energy Storage | Annual O&M Cost | $/participant/year | 84 | Assumption of 5% equipment costs |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceThermal Energy StorageAnnual O&M Cost per MW | WA | General Service | Thermal Energy Storage | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceThermal Energy StorageAnnual Program Administration Cost | WA | General Service | Thermal Energy Storage | Annual Program Administration Cost | $/yr | 19269.4234 | Share of Cost as noted in table at right |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceThermal Energy StorageCost of Equip + Install | WA | General Service | Thermal Energy Storage | Cost of Equip + Install | $/tech | 0 | 0 |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceThermal Energy StorageCost of Equip + Install (per kW basis) | WA | General Service | Thermal Energy Storage | Cost of Equip + Install (per kW basis) | $/kW @meter | 1680 | Utility Dive Article, Ice Energy Implementer cost |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceThermal Energy StorageDe-rate | WA | General Service | Thermal Energy Storage | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceThermal Energy StorageNet to Gross Ratio (free ridership) | WA | General Service | Thermal Energy Storage | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceThermal Energy StoragePer Customer Annual Marketing/Recruitment Cost | WA | General Service | Thermal Energy Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 100 | Assumption $100 for RAP C&I, MAP = RAPx1.2 |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceThermal Energy StoragePer Participant Annual Incentive | WA | General Service | Thermal Energy Storage | Per Participant Annual Incentive | $/participant/year | 0 | No incentive. Program purchases & installs unit. |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceThermal Energy StoragePer kW Annual Incentive | WA | General Service | Thermal Energy Storage | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceThermal Energy StorageProgram Development Cost | WA | General Service | Thermal Energy Storage | Program Development Cost | $/program | 24086.7793 | Share of Cost as noted in table at right |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceThermal Energy StorageProgram Life | WA | General Service | Thermal Energy Storage | Program Life | years | 20 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceThermal Energy StorageProgram Start Year | WA | General Service | Thermal Energy Storage | Program Start Year | year | 2026 | 0 |  | General ServiceProgram Start Year | Market PotentialWA
WALarge General ServiceThermal Energy StorageSummer DR Event Hours | WA | Large General Service | Thermal Energy Storage | Summer DR Event Hours | hours/year | 36 | Same as TOU, six hours on peak period each summer |  | Large General ServiceSummer DR Event Hours | Market PotentialWA
WALarge General ServiceThermal Energy StorageWinter DR Event Hours | WA | Large General Service | Thermal Energy Storage | Winter DR Event Hours | hours/year | 0 | 0 |  | Large General ServiceWinter DR Event Hours | Market PotentialWA
WALarge General ServiceThermal Energy StorageAnnual O&M Cost | WA | Large General Service | Thermal Energy Storage | Annual O&M Cost | $/participant/year | 420 | Assumption of 5% equipment costs |  | Large General ServiceAnnual O&M Cost | Market PotentialWA
WALarge General ServiceThermal Energy StorageAnnual O&M Cost per MW | WA | Large General Service | Thermal Energy Storage | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | Large General ServiceAnnual O&M Cost per MW | Market PotentialWA
WALarge General ServiceThermal Energy StorageAnnual Program Administration Cost | WA | Large General Service | Thermal Energy Storage | Annual Program Administration Cost | $/yr | 17653.2826 | Share of Cost as noted in table at right |  | Large General ServiceAnnual Program Administration Cost | Market PotentialWA
WALarge General ServiceThermal Energy StorageCost of Equip + Install | WA | Large General Service | Thermal Energy Storage | Cost of Equip + Install | $/tech | 0 | 0 |  | Large General ServiceCost of Equip + Install | Market PotentialWA
WALarge General ServiceThermal Energy StorageCost of Equip + Install (per kW basis) | WA | Large General Service | Thermal Energy Storage | Cost of Equip + Install (per kW basis) | $/kW @meter | 8400 | Utility Dive Article, Ice Energy Implementer cost |  | Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WALarge General ServiceThermal Energy StorageDe-rate | WA | Large General Service | Thermal Energy Storage | De-rate | capacity equivalence factor | 1 | 0 |  | Large General ServiceDe-rate | Market PotentialWA
WALarge General ServiceThermal Energy StorageNet to Gross Ratio (free ridership) | WA | Large General Service | Thermal Energy Storage | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WALarge General ServiceThermal Energy StoragePer Customer Annual Marketing/Recruitment Cost | WA | Large General Service | Thermal Energy Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 100 | Assumption $100 for RAP C&I, MAP = RAPx1.2 |  | Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WALarge General ServiceThermal Energy StoragePer Participant Annual Incentive | WA | Large General Service | Thermal Energy Storage | Per Participant Annual Incentive | $/participant/year | 0 | No incentive. Program purchases & installs unit. |  | Large General ServicePer Participant Annual Incentive | Market PotentialWA
WALarge General ServiceThermal Energy StoragePer kW Annual Incentive | WA | Large General Service | Thermal Energy Storage | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | Large General ServicePer kW Annual Incentive | Market PotentialWA
WALarge General ServiceThermal Energy StorageProgram Development Cost | WA | Large General Service | Thermal Energy Storage | Program Development Cost | $/program | 22066.6033 | Share of Cost as noted in table at right |  | Large General ServiceProgram Development Cost | Market PotentialWA
WALarge General ServiceThermal Energy StorageProgram Life | WA | Large General Service | Thermal Energy Storage | Program Life | years | 20 | 0 |  | Large General ServiceProgram Life | Market PotentialWA
WALarge General ServiceThermal Energy StorageProgram Start Year | WA | Large General Service | Thermal Energy Storage | Program Start Year | year | 2026 | 0 |  | Large General ServiceProgram Start Year | Market PotentialWA
WAExtra Large General ServiceThermal Energy StorageSummer DR Event Hours | WA | Extra Large General Service | Thermal Energy Storage | Summer DR Event Hours | hours/year | 36 | Same as TOU, six hours on peak period each summer |  | Extra Large General ServiceSummer DR Event Hours | Market PotentialWA
WAExtra Large General ServiceThermal Energy StorageWinter DR Event Hours | WA | Extra Large General Service | Thermal Energy Storage | Winter DR Event Hours | hours/year | 0 | 0 |  | Extra Large General ServiceWinter DR Event Hours | Market PotentialWA
WAExtra Large General ServiceThermal Energy StorageAnnual O&M Cost | WA | Extra Large General Service | Thermal Energy Storage | Annual O&M Cost | $/participant/year | 420 | Assumption of 5% equipment costs |  | Extra Large General ServiceAnnual O&M Cost | Market PotentialWA
WAExtra Large General ServiceThermal Energy StorageAnnual O&M Cost per MW | WA | Extra Large General Service | Thermal Energy Storage | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | Extra Large General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAExtra Large General ServiceThermal Energy StorageAnnual Program Administration Cost | WA | Extra Large General Service | Thermal Energy Storage | Annual Program Administration Cost | $/yr | 213.7787 | Share of Cost as noted in table at right |  | Extra Large General ServiceAnnual Program Administration Cost | Market PotentialWA
WAExtra Large General ServiceThermal Energy StorageCost of Equip + Install | WA | Extra Large General Service | Thermal Energy Storage | Cost of Equip + Install | $/tech | 0 | 0 |  | Extra Large General ServiceCost of Equip + Install | Market PotentialWA
WAExtra Large General ServiceThermal Energy StorageCost of Equip + Install (per kW basis) | WA | Extra Large General Service | Thermal Energy Storage | Cost of Equip + Install (per kW basis) | $/kW @meter | 8400 | Utility Dive Article, Ice Energy Implementer cost |  | Extra Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAExtra Large General ServiceThermal Energy StorageDe-rate | WA | Extra Large General Service | Thermal Energy Storage | De-rate | capacity equivalence factor | 1 | 0 |  | Extra Large General ServiceDe-rate | Market PotentialWA
WAExtra Large General ServiceThermal Energy StorageNet to Gross Ratio (free ridership) | WA | Extra Large General Service | Thermal Energy Storage | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | Extra Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAExtra Large General ServiceThermal Energy StoragePer Customer Annual Marketing/Recruitment Cost | WA | Extra Large General Service | Thermal Energy Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 100 | Assumption $100 for RAP C&I, MAP = RAPx1.2 |  | Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAExtra Large General ServiceThermal Energy StoragePer Participant Annual Incentive | WA | Extra Large General Service | Thermal Energy Storage | Per Participant Annual Incentive | $/participant/year | 0 | No incentive. Program purchases & installs unit. |  | Extra Large General ServicePer Participant Annual Incentive | Market PotentialWA
WAExtra Large General ServiceThermal Energy StoragePer kW Annual Incentive | WA | Extra Large General Service | Thermal Energy Storage | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | Extra Large General ServicePer kW Annual Incentive | Market PotentialWA
WAExtra Large General ServiceThermal Energy StorageProgram Development Cost | WA | Extra Large General Service | Thermal Energy Storage | Program Development Cost | $/program | 267.2234 | Share of Cost as noted in table at right |  | Extra Large General ServiceProgram Development Cost | Market PotentialWA
WAExtra Large General ServiceThermal Energy StorageProgram Life | WA | Extra Large General Service | Thermal Energy Storage | Program Life | years | 20 | 0 |  | Extra Large General ServiceProgram Life | Market PotentialWA
WAExtra Large General ServiceThermal Energy StorageProgram Start Year | WA | Extra Large General Service | Thermal Energy Storage | Program Start Year | year | 2026 | 0 |  | Extra Large General ServiceProgram Start Year | Market PotentialWA
WAResidentialBattery Energy StorageSummer DR Event Hours | WA | Residential | Battery Energy Storage | Summer DR Event Hours | hours/year | 120 | Xcel Energy CO Renewable Battery Connect: up to 60 events per year, assuming 4-hr events. |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialBattery Energy StorageWinter DR Event Hours | WA | Residential | Battery Energy Storage | Winter DR Event Hours | hours/year | 120 | Xcel Energy CO Renewable Battery Connect: up to 60 events per year, assuming 4-hr events. |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialBattery Energy StorageAnnual O&M Cost | WA | Residential | Battery Energy Storage | Annual O&M Cost | $/participant/year | 50 | 2023 PAC CPA: PNNL 2019 ($10/kW per year) |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialBattery Energy StorageAnnual O&M Cost per MW | WA | Residential | Battery Energy Storage | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialBattery Energy StorageAnnual Program Administration Cost | WA | Residential | Battery Energy Storage | Annual Program Administration Cost | $/yr | 33520.2959 | half FTE @ $150,000 |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialBattery Energy StorageCost of Equip + Install | WA | Residential | Battery Energy Storage | Cost of Equip + Install | $/tech | 2500 | Xcel Energy CO Renewable Battery Connect: $500/enrolled kW for enrolling in the program (capped at 50% of battery equipment costs) |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialBattery Energy StorageCost of Equip + Install (per kW basis) | WA | Residential | Battery Energy Storage | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialBattery Energy StorageDe-rate | WA | Residential | Battery Energy Storage | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialBattery Energy StorageNet to Gross Ratio (free ridership) | WA | Residential | Battery Energy Storage | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialBattery Energy StoragePer Customer Annual Marketing/Recruitment Cost | WA | Residential | Battery Energy Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | 0 |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialBattery Energy StoragePer Participant Annual Incentive | WA | Residential | Battery Energy Storage | Per Participant Annual Incentive | $/participant/year | 0 | 0 |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialBattery Energy StoragePer kW Annual Incentive | WA | Residential | Battery Energy Storage | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialBattery Energy StorageProgram Development Cost | WA | Residential | Battery Energy Storage | Program Development Cost | $/program | 41900.3699 | 0 |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialBattery Energy StorageProgram Life | WA | Residential | Battery Energy Storage | Program Life | years | 15 | NREL |  | ResidentialProgram Life | Market PotentialWA
WAResidentialBattery Energy StorageProgram Start Year | WA | Residential | Battery Energy Storage | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServiceBattery Energy StorageSummer DR Event Hours | WA | General Service | Battery Energy Storage | Summer DR Event Hours | hours/year | 120 | Xcel Energy CO Renewable Battery Connect: up to 60 events per year, assuming 4-hr events. |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceBattery Energy StorageWinter DR Event Hours | WA | General Service | Battery Energy Storage | Winter DR Event Hours | hours/year | 120 | Xcel Energy CO Renewable Battery Connect: up to 60 events per year, assuming 4-hr events. |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceBattery Energy StorageAnnual O&M Cost | WA | General Service | Battery Energy Storage | Annual O&M Cost | $/participant/year | 50 | 2023 PAC CPA: PNNL 2019 ($10/kW per year) |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceBattery Energy StorageAnnual O&M Cost per MW | WA | General Service | Battery Energy Storage | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceBattery Energy StorageAnnual Program Administration Cost | WA | General Service | Battery Energy Storage | Annual Program Administration Cost | $/yr | 4920 | half FTE @ $150,000 |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceBattery Energy StorageCost of Equip + Install | WA | General Service | Battery Energy Storage | Cost of Equip + Install | $/tech | 2500 | Xcel Energy CO Renewable Battery Connect: $500/enrolled kW for enrolling in the program (capped at 50% of battery equipment costs) |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceBattery Energy StorageCost of Equip + Install (per kW basis) | WA | General Service | Battery Energy Storage | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceBattery Energy StorageDe-rate | WA | General Service | Battery Energy Storage | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceBattery Energy StorageNet to Gross Ratio (free ridership) | WA | General Service | Battery Energy Storage | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceBattery Energy StoragePer Customer Annual Marketing/Recruitment Cost | WA | General Service | Battery Energy Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | 0 |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceBattery Energy StoragePer Participant Annual Incentive | WA | General Service | Battery Energy Storage | Per Participant Annual Incentive | $/participant/year | 0 | 0 |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceBattery Energy StoragePer kW Annual Incentive | WA | General Service | Battery Energy Storage | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceBattery Energy StorageProgram Development Cost | WA | General Service | Battery Energy Storage | Program Development Cost | $/program | 6150 | 0 |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceBattery Energy StorageProgram Life | WA | General Service | Battery Energy Storage | Program Life | years | 15 | NREL |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceBattery Energy StorageProgram Start Year | WA | General Service | Battery Energy Storage | Program Start Year | year | 2026 | Assumed rollout could piggyback on Utility's TOU |  | General ServiceProgram Start Year | Market PotentialWA
WALarge General ServiceBattery Energy StorageSummer DR Event Hours | WA | Large General Service | Battery Energy Storage | Summer DR Event Hours | hours/year |  |  |  | Large General ServiceSummer DR Event Hours | Market PotentialWA
WALarge General ServiceBattery Energy StorageWinter DR Event Hours | WA | Large General Service | Battery Energy Storage | Winter DR Event Hours | hours/year |  |  |  | Large General ServiceWinter DR Event Hours | Market PotentialWA
WALarge General ServiceBattery Energy StorageAnnual O&M Cost | WA | Large General Service | Battery Energy Storage | Annual O&M Cost | $/participant/year |  |  |  | Large General ServiceAnnual O&M Cost | Market PotentialWA
WALarge General ServiceBattery Energy StorageAnnual O&M Cost per MW | WA | Large General Service | Battery Energy Storage | Annual O&M Cost per MW | $/MW @meter |  |  |  | Large General ServiceAnnual O&M Cost per MW | Market PotentialWA
WALarge General ServiceBattery Energy StorageAnnual Program Administration Cost | WA | Large General Service | Battery Energy Storage | Annual Program Administration Cost | $/yr |  |  |  | Large General ServiceAnnual Program Administration Cost | Market PotentialWA
WALarge General ServiceBattery Energy StorageCost of Equip + Install | WA | Large General Service | Battery Energy Storage | Cost of Equip + Install | $/tech |  |  |  | Large General ServiceCost of Equip + Install | Market PotentialWA
WALarge General ServiceBattery Energy StorageCost of Equip + Install (per kW basis) | WA | Large General Service | Battery Energy Storage | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WALarge General ServiceBattery Energy StorageDe-rate | WA | Large General Service | Battery Energy Storage | De-rate | capacity equivalence factor |  |  |  | Large General ServiceDe-rate | Market PotentialWA
WALarge General ServiceBattery Energy StorageNet to Gross Ratio (free ridership) | WA | Large General Service | Battery Energy Storage | Net to Gross Ratio (free ridership) | ratio |  |  |  | Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WALarge General ServiceBattery Energy StoragePer Customer Annual Marketing/Recruitment Cost | WA | Large General Service | Battery Energy Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WALarge General ServiceBattery Energy StoragePer Participant Annual Incentive | WA | Large General Service | Battery Energy Storage | Per Participant Annual Incentive | $/participant/year |  |  |  | Large General ServicePer Participant Annual Incentive | Market PotentialWA
WALarge General ServiceBattery Energy StoragePer kW Annual Incentive | WA | Large General Service | Battery Energy Storage | Per kW Annual Incentive | $/kW @meter/year |  |  |  | Large General ServicePer kW Annual Incentive | Market PotentialWA
WALarge General ServiceBattery Energy StorageProgram Development Cost | WA | Large General Service | Battery Energy Storage | Program Development Cost | $/program |  |  |  | Large General ServiceProgram Development Cost | Market PotentialWA
WALarge General ServiceBattery Energy StorageProgram Life | WA | Large General Service | Battery Energy Storage | Program Life | years |  |  |  | Large General ServiceProgram Life | Market PotentialWA
WALarge General ServiceBattery Energy StorageProgram Start Year | WA | Large General Service | Battery Energy Storage | Program Start Year | year |  |  |  | Large General ServiceProgram Start Year | Market PotentialWA
WAExtra Large General ServiceBattery Energy StorageSummer DR Event Hours | WA | Extra Large General Service | Battery Energy Storage | Summer DR Event Hours | hours/year |  |  |  | Extra Large General ServiceSummer DR Event Hours | Market PotentialWA
WAExtra Large General ServiceBattery Energy StorageWinter DR Event Hours | WA | Extra Large General Service | Battery Energy Storage | Winter DR Event Hours | hours/year |  |  |  | Extra Large General ServiceWinter DR Event Hours | Market PotentialWA
WAExtra Large General ServiceBattery Energy StorageAnnual O&M Cost | WA | Extra Large General Service | Battery Energy Storage | Annual O&M Cost | $/participant/year |  |  |  | Extra Large General ServiceAnnual O&M Cost | Market PotentialWA
WAExtra Large General ServiceBattery Energy StorageAnnual O&M Cost per MW | WA | Extra Large General Service | Battery Energy Storage | Annual O&M Cost per MW | $/MW @meter |  |  |  | Extra Large General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAExtra Large General ServiceBattery Energy StorageAnnual Program Administration Cost | WA | Extra Large General Service | Battery Energy Storage | Annual Program Administration Cost | $/yr |  |  |  | Extra Large General ServiceAnnual Program Administration Cost | Market PotentialWA
WAExtra Large General ServiceBattery Energy StorageCost of Equip + Install | WA | Extra Large General Service | Battery Energy Storage | Cost of Equip + Install | $/tech |  |  |  | Extra Large General ServiceCost of Equip + Install | Market PotentialWA
WAExtra Large General ServiceBattery Energy StorageCost of Equip + Install (per kW basis) | WA | Extra Large General Service | Battery Energy Storage | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | Extra Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAExtra Large General ServiceBattery Energy StorageDe-rate | WA | Extra Large General Service | Battery Energy Storage | De-rate | capacity equivalence factor |  |  |  | Extra Large General ServiceDe-rate | Market PotentialWA
WAExtra Large General ServiceBattery Energy StorageNet to Gross Ratio (free ridership) | WA | Extra Large General Service | Battery Energy Storage | Net to Gross Ratio (free ridership) | ratio |  |  |  | Extra Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAExtra Large General ServiceBattery Energy StoragePer Customer Annual Marketing/Recruitment Cost | WA | Extra Large General Service | Battery Energy Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAExtra Large General ServiceBattery Energy StoragePer Participant Annual Incentive | WA | Extra Large General Service | Battery Energy Storage | Per Participant Annual Incentive | $/participant/year |  |  |  | Extra Large General ServicePer Participant Annual Incentive | Market PotentialWA
WAExtra Large General ServiceBattery Energy StoragePer kW Annual Incentive | WA | Extra Large General Service | Battery Energy Storage | Per kW Annual Incentive | $/kW @meter/year |  |  |  | Extra Large General ServicePer kW Annual Incentive | Market PotentialWA
WAExtra Large General ServiceBattery Energy StorageProgram Development Cost | WA | Extra Large General Service | Battery Energy Storage | Program Development Cost | $/program |  |  |  | Extra Large General ServiceProgram Development Cost | Market PotentialWA
WAExtra Large General ServiceBattery Energy StorageProgram Life | WA | Extra Large General Service | Battery Energy Storage | Program Life | years |  |  |  | Extra Large General ServiceProgram Life | Market PotentialWA
WAExtra Large General ServiceBattery Energy StorageProgram Start Year | WA | Extra Large General Service | Battery Energy Storage | Program Start Year | year |  |  |  | Extra Large General ServiceProgram Start Year | Market PotentialWA
WAResidentialAncillary Battery StorageSummer DR Event Hours | WA | Residential | Ancillary Battery Storage | Summer DR Event Hours | hours/year | 36 | 0 |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialAncillary Battery StorageWinter DR Event Hours | WA | Residential | Ancillary Battery Storage | Winter DR Event Hours | hours/year | 36 | Round trip efficiency assumption: |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialAncillary Battery StorageAnnual O&M Cost | WA | Residential | Ancillary Battery Storage | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialAncillary Battery StorageAnnual O&M Cost per MW | WA | Residential | Ancillary Battery Storage | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialAncillary Battery StorageAnnual Program Administration Cost | WA | Residential | Ancillary Battery Storage | Annual Program Administration Cost | $/yr | 33520.2959 | half FTE @ $150,000 |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialAncillary Battery StorageCost of Equip + Install | WA | Residential | Ancillary Battery Storage | Cost of Equip + Install | $/tech | 0 | Customer already has device if on program |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialAncillary Battery StorageCost of Equip + Install (per kW basis) | WA | Residential | Ancillary Battery Storage | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialAncillary Battery StorageDe-rate | WA | Residential | Ancillary Battery Storage | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialAncillary Battery StorageNet to Gross Ratio (free ridership) | WA | Residential | Ancillary Battery Storage | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialAncillary Battery StoragePer Customer Annual Marketing/Recruitment Cost | WA | Residential | Ancillary Battery Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | 0 |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialAncillary Battery StoragePer Participant Annual Incentive | WA | Residential | Ancillary Battery Storage | Per Participant Annual Incentive | $/participant/year | 20 | $20 incentives to participate in ancillary |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialAncillary Battery StoragePer kW Annual Incentive | WA | Residential | Ancillary Battery Storage | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialAncillary Battery StorageProgram Development Cost | WA | Residential | Ancillary Battery Storage | Program Development Cost | $/program | 41900.3699 | 0 |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialAncillary Battery StorageProgram Life | WA | Residential | Ancillary Battery Storage | Program Life | years | 15 | NREL |  | ResidentialProgram Life | Market PotentialWA
WAResidentialAncillary Battery StorageProgram Start Year | WA | Residential | Ancillary Battery Storage | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServiceAncillary Battery StorageSummer DR Event Hours | WA | General Service | Ancillary Battery Storage | Summer DR Event Hours | hours/year | 36 | 0 |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceAncillary Battery StorageWinter DR Event Hours | WA | General Service | Ancillary Battery Storage | Winter DR Event Hours | hours/year | 36 | Round trip efficiency assumption: |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceAncillary Battery StorageAnnual O&M Cost | WA | General Service | Ancillary Battery Storage | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceAncillary Battery StorageAnnual O&M Cost per MW | WA | General Service | Ancillary Battery Storage | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceAncillary Battery StorageAnnual Program Administration Cost | WA | General Service | Ancillary Battery Storage | Annual Program Administration Cost | $/yr | 4920 | half FTE @ $150,000 |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceAncillary Battery StorageCost of Equip + Install | WA | General Service | Ancillary Battery Storage | Cost of Equip + Install | $/tech | 0 | Customer already has device if on program |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceAncillary Battery StorageCost of Equip + Install (per kW basis) | WA | General Service | Ancillary Battery Storage | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceAncillary Battery StorageDe-rate | WA | General Service | Ancillary Battery Storage | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceAncillary Battery StorageNet to Gross Ratio (free ridership) | WA | General Service | Ancillary Battery Storage | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceAncillary Battery StoragePer Customer Annual Marketing/Recruitment Cost | WA | General Service | Ancillary Battery Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | 0 |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceAncillary Battery StoragePer Participant Annual Incentive | WA | General Service | Ancillary Battery Storage | Per Participant Annual Incentive | $/participant/year | 20 | $20 incentives to participate in ancillary |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceAncillary Battery StoragePer kW Annual Incentive | WA | General Service | Ancillary Battery Storage | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceAncillary Battery StorageProgram Development Cost | WA | General Service | Ancillary Battery Storage | Program Development Cost | $/program | 6150 | 0 |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceAncillary Battery StorageProgram Life | WA | General Service | Ancillary Battery Storage | Program Life | years | 15 | NREL |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceAncillary Battery StorageProgram Start Year | WA | General Service | Ancillary Battery Storage | Program Start Year | year | 2026 | Assumed rollout could piggyback on Utility's TOU |  | General ServiceProgram Start Year | Market PotentialWA
WALarge General ServiceAncillary Battery StorageSummer DR Event Hours | WA | Large General Service | Ancillary Battery Storage | Summer DR Event Hours | hours/year |  |  |  | Large General ServiceSummer DR Event Hours | Market PotentialWA
WALarge General ServiceAncillary Battery StorageWinter DR Event Hours | WA | Large General Service | Ancillary Battery Storage | Winter DR Event Hours | hours/year |  |  |  | Large General ServiceWinter DR Event Hours | Market PotentialWA
WALarge General ServiceAncillary Battery StorageAnnual O&M Cost | WA | Large General Service | Ancillary Battery Storage | Annual O&M Cost | $/participant/year |  |  |  | Large General ServiceAnnual O&M Cost | Market PotentialWA
WALarge General ServiceAncillary Battery StorageAnnual O&M Cost per MW | WA | Large General Service | Ancillary Battery Storage | Annual O&M Cost per MW | $/MW @meter |  |  |  | Large General ServiceAnnual O&M Cost per MW | Market PotentialWA
WALarge General ServiceAncillary Battery StorageAnnual Program Administration Cost | WA | Large General Service | Ancillary Battery Storage | Annual Program Administration Cost | $/yr |  |  |  | Large General ServiceAnnual Program Administration Cost | Market PotentialWA
WALarge General ServiceAncillary Battery StorageCost of Equip + Install | WA | Large General Service | Ancillary Battery Storage | Cost of Equip + Install | $/tech |  |  |  | Large General ServiceCost of Equip + Install | Market PotentialWA
WALarge General ServiceAncillary Battery StorageCost of Equip + Install (per kW basis) | WA | Large General Service | Ancillary Battery Storage | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WALarge General ServiceAncillary Battery StorageDe-rate | WA | Large General Service | Ancillary Battery Storage | De-rate | capacity equivalence factor |  |  |  | Large General ServiceDe-rate | Market PotentialWA
WALarge General ServiceAncillary Battery StorageNet to Gross Ratio (free ridership) | WA | Large General Service | Ancillary Battery Storage | Net to Gross Ratio (free ridership) | ratio |  |  |  | Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WALarge General ServiceAncillary Battery StoragePer Customer Annual Marketing/Recruitment Cost | WA | Large General Service | Ancillary Battery Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WALarge General ServiceAncillary Battery StoragePer Participant Annual Incentive | WA | Large General Service | Ancillary Battery Storage | Per Participant Annual Incentive | $/participant/year |  |  |  | Large General ServicePer Participant Annual Incentive | Market PotentialWA
WALarge General ServiceAncillary Battery StoragePer kW Annual Incentive | WA | Large General Service | Ancillary Battery Storage | Per kW Annual Incentive | $/kW @meter/year |  |  |  | Large General ServicePer kW Annual Incentive | Market PotentialWA
WALarge General ServiceAncillary Battery StorageProgram Development Cost | WA | Large General Service | Ancillary Battery Storage | Program Development Cost | $/program |  |  |  | Large General ServiceProgram Development Cost | Market PotentialWA
WALarge General ServiceAncillary Battery StorageProgram Life | WA | Large General Service | Ancillary Battery Storage | Program Life | years |  |  |  | Large General ServiceProgram Life | Market PotentialWA
WALarge General ServiceAncillary Battery StorageProgram Start Year | WA | Large General Service | Ancillary Battery Storage | Program Start Year | year |  |  |  | Large General ServiceProgram Start Year | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StorageSummer DR Event Hours | WA | Extra Large General Service | Ancillary Battery Storage | Summer DR Event Hours | hours/year |  |  |  | Extra Large General ServiceSummer DR Event Hours | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StorageWinter DR Event Hours | WA | Extra Large General Service | Ancillary Battery Storage | Winter DR Event Hours | hours/year |  |  |  | Extra Large General ServiceWinter DR Event Hours | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StorageAnnual O&M Cost | WA | Extra Large General Service | Ancillary Battery Storage | Annual O&M Cost | $/participant/year |  |  |  | Extra Large General ServiceAnnual O&M Cost | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StorageAnnual O&M Cost per MW | WA | Extra Large General Service | Ancillary Battery Storage | Annual O&M Cost per MW | $/MW @meter |  |  |  | Extra Large General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StorageAnnual Program Administration Cost | WA | Extra Large General Service | Ancillary Battery Storage | Annual Program Administration Cost | $/yr |  |  |  | Extra Large General ServiceAnnual Program Administration Cost | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StorageCost of Equip + Install | WA | Extra Large General Service | Ancillary Battery Storage | Cost of Equip + Install | $/tech |  |  |  | Extra Large General ServiceCost of Equip + Install | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StorageCost of Equip + Install (per kW basis) | WA | Extra Large General Service | Ancillary Battery Storage | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | Extra Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StorageDe-rate | WA | Extra Large General Service | Ancillary Battery Storage | De-rate | capacity equivalence factor |  |  |  | Extra Large General ServiceDe-rate | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StorageNet to Gross Ratio (free ridership) | WA | Extra Large General Service | Ancillary Battery Storage | Net to Gross Ratio (free ridership) | ratio |  |  |  | Extra Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StoragePer Customer Annual Marketing/Recruitment Cost | WA | Extra Large General Service | Ancillary Battery Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StoragePer Participant Annual Incentive | WA | Extra Large General Service | Ancillary Battery Storage | Per Participant Annual Incentive | $/participant/year |  |  |  | Extra Large General ServicePer Participant Annual Incentive | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StoragePer kW Annual Incentive | WA | Extra Large General Service | Ancillary Battery Storage | Per kW Annual Incentive | $/kW @meter/year |  |  |  | Extra Large General ServicePer kW Annual Incentive | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StorageProgram Development Cost | WA | Extra Large General Service | Ancillary Battery Storage | Program Development Cost | $/program |  |  |  | Extra Large General ServiceProgram Development Cost | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StorageProgram Life | WA | Extra Large General Service | Ancillary Battery Storage | Program Life | years |  |  |  | Extra Large General ServiceProgram Life | Market PotentialWA
WAExtra Large General ServiceAncillary Battery StorageProgram Start Year | WA | Extra Large General Service | Ancillary Battery Storage | Program Start Year | year |  |  |  | Extra Large General ServiceProgram Start Year | Market PotentialWA
WAResidentialBehavioralSummer DR Event Hours | WA | Residential | Behavioral | Summer DR Event Hours | hours/year | 40 | 8 hour event window x 5 events, Consumers Energy 7am-8pm 8 hr window |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialBehavioralWinter DR Event Hours | WA | Residential | Behavioral | Winter DR Event Hours | hours/year | 40 | 8 hour event window x 5 events, Consumers Energy 7am-8pm 8 hr window |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialBehavioralAnnual O&M Cost | WA | Residential | Behavioral | Annual O&M Cost | $/participant/year | 3.25 | Oracle interview on 8/30, estimation of admin cost per household - KM heard 3 - 3.5 all inclusive- Implementation Cost |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialBehavioralAnnual O&M Cost per MW | WA | Residential | Behavioral | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialBehavioralAnnual Program Administration Cost | WA | Residential | Behavioral | Annual Program Administration Cost | $/yr | 40099.4232 | 0 |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialBehavioralCost of Equip + Install | WA | Residential | Behavioral | Cost of Equip + Install | $/tech | 0 | 0 |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialBehavioralCost of Equip + Install (per kW basis) | WA | Residential | Behavioral | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialBehavioralDe-rate | WA | Residential | Behavioral | De-rate | capacity equivalence factor | 1 | Impact Reduced to reflect diminished savings program pulls in participants who are not "high" users |  | ResidentialDe-rate | Market PotentialWA
WAResidentialBehavioralNet to Gross Ratio (free ridership) | WA | Residential | Behavioral | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialBehavioralPer Customer Annual Marketing/Recruitment Cost | WA | Residential | Behavioral | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | 0 |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialBehavioralPer Participant Annual Incentive | WA | Residential | Behavioral | Per Participant Annual Incentive | $/participant/year | 0 | No Incentive for Behavioral DR - Brattle PGE Potential Study 2016 - |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialBehavioralPer kW Annual Incentive | WA | Residential | Behavioral | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialBehavioralProgram Development Cost | WA | Residential | Behavioral | Program Development Cost | $/program | 66832.372 | 0 |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialBehavioralProgram Life | WA | Residential | Behavioral | Program Life | years | 1 | MISO Res LoadMAP DSM Programs.xlsx (LRZ7) - Lifetime |  | ResidentialProgram Life | Market PotentialWA
WAResidentialBehavioralProgram Start Year | WA | Residential | Behavioral | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inSummer DR Event Hours | WA | Residential | Pilot-Time-of-Use Opt-in | Summer DR Event Hours | hours/year | 528 | Six hours on-peak period each summer weekday |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inWinter DR Event Hours | WA | Residential | Pilot-Time-of-Use Opt-in | Winter DR Event Hours | hours/year | 528 | Six hours on-peak period each winter weekday too, except for Utah |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inAnnual O&M Cost | WA | Residential | Pilot-Time-of-Use Opt-in | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inAnnual O&M Cost per MW | WA | Residential | Pilot-Time-of-Use Opt-in | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inAnnual Program Administration Cost | WA | Residential | Pilot-Time-of-Use Opt-in | Annual Program Administration Cost | $/yr | 53751.0005 | 0 |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inCost of Equip + Install | WA | Residential | Pilot-Time-of-Use Opt-in | Cost of Equip + Install | $/tech | 0 | 0 |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inCost of Equip + Install (per kW basis) | WA | Residential | Pilot-Time-of-Use Opt-in | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inDe-rate | WA | Residential | Pilot-Time-of-Use Opt-in | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inNet to Gross Ratio (free ridership) | WA | Residential | Pilot-Time-of-Use Opt-in | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inPer Customer Annual Marketing/Recruitment Cost | WA | Residential | Pilot-Time-of-Use Opt-in | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | 1.5x standatd $50 marketing cost because it involves more education on kW rate blocks |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inPer Participant Annual Incentive | WA | Residential | Pilot-Time-of-Use Opt-in | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inPer kW Annual Incentive | WA | Residential | Pilot-Time-of-Use Opt-in | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inProgram Development Cost | WA | Residential | Pilot-Time-of-Use Opt-in | Program Development Cost | $/program | 537510.0049 | 0 |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inProgram Life | WA | Residential | Pilot-Time-of-Use Opt-in | Program Life | years | 10 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialPilot-Time-of-Use Opt-inProgram Start Year | WA | Residential | Pilot-Time-of-Use Opt-in | Program Start Year | year | 2024 | Modeling potential pilot starting in 2024 |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inSummer DR Event Hours | WA | General Service | Pilot-Time-of-Use Opt-in | Summer DR Event Hours | hours/year | 528 | Six hours on-peak period each summer weekday |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inWinter DR Event Hours | WA | General Service | Pilot-Time-of-Use Opt-in | Winter DR Event Hours | hours/year | 528 | Six hours on-peak period each winter weekday too, except for Utah |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inAnnual O&M Cost | WA | General Service | Pilot-Time-of-Use Opt-in | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inAnnual O&M Cost per MW | WA | General Service | Pilot-Time-of-Use Opt-in | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inAnnual Program Administration Cost | WA | General Service | Pilot-Time-of-Use Opt-in | Annual Program Administration Cost | $/yr | 13357.8494 | 0 |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inCost of Equip + Install | WA | General Service | Pilot-Time-of-Use Opt-in | Cost of Equip + Install | $/tech | 0 | 0 |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inCost of Equip + Install (per kW basis) | WA | General Service | Pilot-Time-of-Use Opt-in | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inDe-rate | WA | General Service | Pilot-Time-of-Use Opt-in | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inNet to Gross Ratio (free ridership) | WA | General Service | Pilot-Time-of-Use Opt-in | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inPer Customer Annual Marketing/Recruitment Cost | WA | General Service | Pilot-Time-of-Use Opt-in | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | 1.5x standatd $50 marketing cost because it involves more education on kW rate blocks |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inPer Participant Annual Incentive | WA | General Service | Pilot-Time-of-Use Opt-in | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inPer kW Annual Incentive | WA | General Service | Pilot-Time-of-Use Opt-in | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inProgram Development Cost | WA | General Service | Pilot-Time-of-Use Opt-in | Program Development Cost | $/program | 133578.494 | 0 |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inProgram Life | WA | General Service | Pilot-Time-of-Use Opt-in | Program Life | years | 10 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServicePilot-Time-of-Use Opt-inProgram Start Year | WA | General Service | Pilot-Time-of-Use Opt-in | Program Start Year | year | 2024 | Modeling potential pilot starting in 2024 |  | General ServiceProgram Start Year | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inSummer DR Event Hours | WA | Residential | Parent-Time-of-Use Opt-in | Summer DR Event Hours | hours/year | 528 | Six hours on-peak period each summer weekday |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inWinter DR Event Hours | WA | Residential | Parent-Time-of-Use Opt-in | Winter DR Event Hours | hours/year | 528 | Six hours on-peak period each winter weekday too, except for Utah |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inAnnual O&M Cost | WA | Residential | Parent-Time-of-Use Opt-in | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inAnnual O&M Cost per MW | WA | Residential | Parent-Time-of-Use Opt-in | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inAnnual Program Administration Cost | WA | Residential | Parent-Time-of-Use Opt-in | Annual Program Administration Cost | $/yr | 134382.8763 | 2024 Avista Update |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inCost of Equip + Install | WA | Residential | Parent-Time-of-Use Opt-in | Cost of Equip + Install | $/tech | 0 | 0 |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inCost of Equip + Install (per kW basis) | WA | Residential | Parent-Time-of-Use Opt-in | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inDe-rate | WA | Residential | Parent-Time-of-Use Opt-in | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inNet to Gross Ratio (free ridership) | WA | Residential | Parent-Time-of-Use Opt-in | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inPer Customer Annual Marketing/Recruitment Cost | WA | Residential | Parent-Time-of-Use Opt-in | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | 2024 Avista Update |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inPer Participant Annual Incentive | WA | Residential | Parent-Time-of-Use Opt-in | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inPer kW Annual Incentive | WA | Residential | Parent-Time-of-Use Opt-in | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inProgram Development Cost | WA | Residential | Parent-Time-of-Use Opt-in | Program Development Cost | $/program | 0 | 2024 Avista Update- WA dev costs are sunk($2 mil), ID costs will be half of WA @ $1mil dev costs |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inProgram Life | WA | Residential | Parent-Time-of-Use Opt-in | Program Life | years | 10 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialParent-Time-of-Use Opt-inProgram Start Year | WA | Residential | Parent-Time-of-Use Opt-in | Program Start Year | year | 2025 | WA; ID Start in 2028: 2024 Avista Update; will change ramp rate after model run |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inSummer DR Event Hours | WA | General Service | Parent-Time-of-Use Opt-in | Summer DR Event Hours | hours/year | 528 | Six hours on-peak period each summer weekday |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inWinter DR Event Hours | WA | General Service | Parent-Time-of-Use Opt-in | Winter DR Event Hours | hours/year | 528 | Six hours on-peak period each winter weekday too, except for Utah |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inAnnual O&M Cost | WA | General Service | Parent-Time-of-Use Opt-in | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inAnnual O&M Cost per MW | WA | General Service | Parent-Time-of-Use Opt-in | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inAnnual Program Administration Cost | WA | General Service | Parent-Time-of-Use Opt-in | Annual Program Administration Cost | $/yr | 33395.9593 | 2024 Avista Update |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inCost of Equip + Install | WA | General Service | Parent-Time-of-Use Opt-in | Cost of Equip + Install | $/tech | 0 | 0 |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inCost of Equip + Install (per kW basis) | WA | General Service | Parent-Time-of-Use Opt-in | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inDe-rate | WA | General Service | Parent-Time-of-Use Opt-in | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inNet to Gross Ratio (free ridership) | WA | General Service | Parent-Time-of-Use Opt-in | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inPer Customer Annual Marketing/Recruitment Cost | WA | General Service | Parent-Time-of-Use Opt-in | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | 2024 Avista Update |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inPer Participant Annual Incentive | WA | General Service | Parent-Time-of-Use Opt-in | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inPer kW Annual Incentive | WA | General Service | Parent-Time-of-Use Opt-in | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inProgram Development Cost | WA | General Service | Parent-Time-of-Use Opt-in | Program Development Cost | $/program | 133578.494 | 2024 Avista Update- WA dev costs are sunk($2 mil), ID costs will be half of WA @ $1mil dev costs |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inProgram Life | WA | General Service | Parent-Time-of-Use Opt-in | Program Life | years | 10 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceParent-Time-of-Use Opt-inProgram Start Year | WA | General Service | Parent-Time-of-Use Opt-in | Program Start Year | year | 2025 | WA; ID Start in 2028: 2024 Avista Update; will change ramp rate after model run |  | General ServiceProgram Start Year | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inSummer DR Event Hours | WA | Large General Service | Parent-Time-of-Use Opt-in | Summer DR Event Hours | hours/year |  |  |  | Large General ServiceSummer DR Event Hours | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inWinter DR Event Hours | WA | Large General Service | Parent-Time-of-Use Opt-in | Winter DR Event Hours | hours/year |  |  |  | Large General ServiceWinter DR Event Hours | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inAnnual O&M Cost | WA | Large General Service | Parent-Time-of-Use Opt-in | Annual O&M Cost | $/participant/year |  |  |  | Large General ServiceAnnual O&M Cost | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inAnnual O&M Cost per MW | WA | Large General Service | Parent-Time-of-Use Opt-in | Annual O&M Cost per MW | $/MW @meter |  |  |  | Large General ServiceAnnual O&M Cost per MW | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inAnnual Program Administration Cost | WA | Large General Service | Parent-Time-of-Use Opt-in | Annual Program Administration Cost | $/yr |  |  |  | Large General ServiceAnnual Program Administration Cost | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inCost of Equip + Install | WA | Large General Service | Parent-Time-of-Use Opt-in | Cost of Equip + Install | $/tech |  |  |  | Large General ServiceCost of Equip + Install | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inCost of Equip + Install (per kW basis) | WA | Large General Service | Parent-Time-of-Use Opt-in | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inDe-rate | WA | Large General Service | Parent-Time-of-Use Opt-in | De-rate | capacity equivalence factor |  |  |  | Large General ServiceDe-rate | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inNet to Gross Ratio (free ridership) | WA | Large General Service | Parent-Time-of-Use Opt-in | Net to Gross Ratio (free ridership) | ratio |  |  |  | Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inPer Customer Annual Marketing/Recruitment Cost | WA | Large General Service | Parent-Time-of-Use Opt-in | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inPer Participant Annual Incentive | WA | Large General Service | Parent-Time-of-Use Opt-in | Per Participant Annual Incentive | $/participant/year |  |  |  | Large General ServicePer Participant Annual Incentive | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inPer kW Annual Incentive | WA | Large General Service | Parent-Time-of-Use Opt-in | Per kW Annual Incentive | $/kW @meter/year |  |  |  | Large General ServicePer kW Annual Incentive | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inProgram Development Cost | WA | Large General Service | Parent-Time-of-Use Opt-in | Program Development Cost | $/program |  |  |  | Large General ServiceProgram Development Cost | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inProgram Life | WA | Large General Service | Parent-Time-of-Use Opt-in | Program Life | years |  |  |  | Large General ServiceProgram Life | Market PotentialWA
WALarge General ServiceParent-Time-of-Use Opt-inProgram Start Year | WA | Large General Service | Parent-Time-of-Use Opt-in | Program Start Year | year |  |  |  | Large General ServiceProgram Start Year | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inSummer DR Event Hours | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Summer DR Event Hours | hours/year |  |  |  | Extra Large General ServiceSummer DR Event Hours | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inWinter DR Event Hours | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Winter DR Event Hours | hours/year |  |  |  | Extra Large General ServiceWinter DR Event Hours | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inAnnual O&M Cost | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Annual O&M Cost | $/participant/year |  |  |  | Extra Large General ServiceAnnual O&M Cost | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inAnnual O&M Cost per MW | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Annual O&M Cost per MW | $/MW @meter |  |  |  | Extra Large General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inAnnual Program Administration Cost | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Annual Program Administration Cost | $/yr |  |  |  | Extra Large General ServiceAnnual Program Administration Cost | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inCost of Equip + Install | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Cost of Equip + Install | $/tech |  |  |  | Extra Large General ServiceCost of Equip + Install | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inCost of Equip + Install (per kW basis) | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | Extra Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inDe-rate | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | De-rate | capacity equivalence factor |  |  |  | Extra Large General ServiceDe-rate | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inNet to Gross Ratio (free ridership) | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Net to Gross Ratio (free ridership) | ratio |  |  |  | Extra Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inPer Customer Annual Marketing/Recruitment Cost | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inPer Participant Annual Incentive | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Per Participant Annual Incentive | $/participant/year |  |  |  | Extra Large General ServicePer Participant Annual Incentive | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inPer kW Annual Incentive | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Per kW Annual Incentive | $/kW @meter/year |  |  |  | Extra Large General ServicePer kW Annual Incentive | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inProgram Development Cost | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Program Development Cost | $/program |  |  |  | Extra Large General ServiceProgram Development Cost | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inProgram Life | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Program Life | years |  |  |  | Extra Large General ServiceProgram Life | Market PotentialWA
WAExtra Large General ServiceParent-Time-of-Use Opt-inProgram Start Year | WA | Extra Large General Service | Parent-Time-of-Use Opt-in | Program Start Year | year |  |  |  | Extra Large General ServiceProgram Start Year | Market PotentialWA
WAResidentialTime-of-Use Opt-OutSummer DR Event Hours | WA | Residential | Time-of-Use Opt-Out | Summer DR Event Hours | hours/year | 528 | Six hours on-peak period each summer weekday |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialTime-of-Use Opt-OutWinter DR Event Hours | WA | Residential | Time-of-Use Opt-Out | Winter DR Event Hours | hours/year | 528 | Six hours on-peak period each winter weekday too, except for Utah |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialTime-of-Use Opt-OutAnnual O&M Cost | WA | Residential | Time-of-Use Opt-Out | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialTime-of-Use Opt-OutAnnual O&M Cost per MW | WA | Residential | Time-of-Use Opt-Out | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialTime-of-Use Opt-OutAnnual Program Administration Cost | WA | Residential | Time-of-Use Opt-Out | Annual Program Administration Cost | $/yr | 118669.9817 | 2024 Avista Update |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialTime-of-Use Opt-OutCost of Equip + Install | WA | Residential | Time-of-Use Opt-Out | Cost of Equip + Install | $/tech | 0 | 0 |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialTime-of-Use Opt-OutCost of Equip + Install (per kW basis) | WA | Residential | Time-of-Use Opt-Out | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialTime-of-Use Opt-OutDe-rate | WA | Residential | Time-of-Use Opt-Out | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialTime-of-Use Opt-OutNet to Gross Ratio (free ridership) | WA | Residential | Time-of-Use Opt-Out | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialTime-of-Use Opt-OutPer Customer Annual Marketing/Recruitment Cost | WA | Residential | Time-of-Use Opt-Out | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | 2024 Avista Update |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialTime-of-Use Opt-OutPer Participant Annual Incentive | WA | Residential | Time-of-Use Opt-Out | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialTime-of-Use Opt-OutPer kW Annual Incentive | WA | Residential | Time-of-Use Opt-Out | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialTime-of-Use Opt-OutProgram Development Cost | WA | Residential | Time-of-Use Opt-Out | Program Development Cost | $/program | 711991.4105 | 2024 Avista Update |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialTime-of-Use Opt-OutProgram Life | WA | Residential | Time-of-Use Opt-Out | Program Life | years | 10 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialTime-of-Use Opt-OutProgram Start Year | WA | Residential | Time-of-Use Opt-Out | Program Start Year | year | 2025 | 2024 Avista Update |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutSummer DR Event Hours | WA | General Service | Time-of-Use Opt-Out | Summer DR Event Hours | hours/year | 528 | Six hours on-peak period each summer weekday |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutWinter DR Event Hours | WA | General Service | Time-of-Use Opt-Out | Winter DR Event Hours | hours/year | 528 | Six hours on-peak period each winter weekday too, except for Utah |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutAnnual O&M Cost | WA | General Service | Time-of-Use Opt-Out | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutAnnual O&M Cost per MW | WA | General Service | Time-of-Use Opt-Out | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutAnnual Program Administration Cost | WA | General Service | Time-of-Use Opt-Out | Annual Program Administration Cost | $/yr | 49440.9497 | 2024 Avista Update |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutCost of Equip + Install | WA | General Service | Time-of-Use Opt-Out | Cost of Equip + Install | $/tech | 0 | 0 |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutCost of Equip + Install (per kW basis) | WA | General Service | Time-of-Use Opt-Out | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutDe-rate | WA | General Service | Time-of-Use Opt-Out | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutNet to Gross Ratio (free ridership) | WA | General Service | Time-of-Use Opt-Out | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutPer Customer Annual Marketing/Recruitment Cost | WA | General Service | Time-of-Use Opt-Out | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | 2024 Avista Update |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutPer Participant Annual Incentive | WA | General Service | Time-of-Use Opt-Out | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutPer kW Annual Incentive | WA | General Service | Time-of-Use Opt-Out | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutProgram Development Cost | WA | General Service | Time-of-Use Opt-Out | Program Development Cost | $/program | 296633.8329 | 2024 Avista Update |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutProgram Life | WA | General Service | Time-of-Use Opt-Out | Program Life | years | 10 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceTime-of-Use Opt-OutProgram Start Year | WA | General Service | Time-of-Use Opt-Out | Program Start Year | year | 2025 | 0 |  | General ServiceProgram Start Year | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutSummer DR Event Hours | WA | Large General Service | Time-of-Use Opt-Out | Summer DR Event Hours | hours/year |  |  |  | Large General ServiceSummer DR Event Hours | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutWinter DR Event Hours | WA | Large General Service | Time-of-Use Opt-Out | Winter DR Event Hours | hours/year |  |  |  | Large General ServiceWinter DR Event Hours | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutAnnual O&M Cost | WA | Large General Service | Time-of-Use Opt-Out | Annual O&M Cost | $/participant/year |  |  |  | Large General ServiceAnnual O&M Cost | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutAnnual O&M Cost per MW | WA | Large General Service | Time-of-Use Opt-Out | Annual O&M Cost per MW | $/MW @meter |  |  |  | Large General ServiceAnnual O&M Cost per MW | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutAnnual Program Administration Cost | WA | Large General Service | Time-of-Use Opt-Out | Annual Program Administration Cost | $/yr |  |  |  | Large General ServiceAnnual Program Administration Cost | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutCost of Equip + Install | WA | Large General Service | Time-of-Use Opt-Out | Cost of Equip + Install | $/tech |  |  |  | Large General ServiceCost of Equip + Install | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutCost of Equip + Install (per kW basis) | WA | Large General Service | Time-of-Use Opt-Out | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutDe-rate | WA | Large General Service | Time-of-Use Opt-Out | De-rate | capacity equivalence factor |  |  |  | Large General ServiceDe-rate | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutNet to Gross Ratio (free ridership) | WA | Large General Service | Time-of-Use Opt-Out | Net to Gross Ratio (free ridership) | ratio |  |  |  | Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutPer Customer Annual Marketing/Recruitment Cost | WA | Large General Service | Time-of-Use Opt-Out | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutPer Participant Annual Incentive | WA | Large General Service | Time-of-Use Opt-Out | Per Participant Annual Incentive | $/participant/year |  |  |  | Large General ServicePer Participant Annual Incentive | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutPer kW Annual Incentive | WA | Large General Service | Time-of-Use Opt-Out | Per kW Annual Incentive | $/kW @meter/year |  |  |  | Large General ServicePer kW Annual Incentive | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutProgram Development Cost | WA | Large General Service | Time-of-Use Opt-Out | Program Development Cost | $/program |  |  |  | Large General ServiceProgram Development Cost | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutProgram Life | WA | Large General Service | Time-of-Use Opt-Out | Program Life | years |  |  |  | Large General ServiceProgram Life | Market PotentialWA
WALarge General ServiceTime-of-Use Opt-OutProgram Start Year | WA | Large General Service | Time-of-Use Opt-Out | Program Start Year | year |  |  |  | Large General ServiceProgram Start Year | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutSummer DR Event Hours | WA | Extra Large General Service | Time-of-Use Opt-Out | Summer DR Event Hours | hours/year |  |  |  | Extra Large General ServiceSummer DR Event Hours | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutWinter DR Event Hours | WA | Extra Large General Service | Time-of-Use Opt-Out | Winter DR Event Hours | hours/year |  |  |  | Extra Large General ServiceWinter DR Event Hours | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutAnnual O&M Cost | WA | Extra Large General Service | Time-of-Use Opt-Out | Annual O&M Cost | $/participant/year |  |  |  | Extra Large General ServiceAnnual O&M Cost | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutAnnual O&M Cost per MW | WA | Extra Large General Service | Time-of-Use Opt-Out | Annual O&M Cost per MW | $/MW @meter |  |  |  | Extra Large General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutAnnual Program Administration Cost | WA | Extra Large General Service | Time-of-Use Opt-Out | Annual Program Administration Cost | $/yr |  |  |  | Extra Large General ServiceAnnual Program Administration Cost | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutCost of Equip + Install | WA | Extra Large General Service | Time-of-Use Opt-Out | Cost of Equip + Install | $/tech |  |  |  | Extra Large General ServiceCost of Equip + Install | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutCost of Equip + Install (per kW basis) | WA | Extra Large General Service | Time-of-Use Opt-Out | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | Extra Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutDe-rate | WA | Extra Large General Service | Time-of-Use Opt-Out | De-rate | capacity equivalence factor |  |  |  | Extra Large General ServiceDe-rate | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutNet to Gross Ratio (free ridership) | WA | Extra Large General Service | Time-of-Use Opt-Out | Net to Gross Ratio (free ridership) | ratio |  |  |  | Extra Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutPer Customer Annual Marketing/Recruitment Cost | WA | Extra Large General Service | Time-of-Use Opt-Out | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutPer Participant Annual Incentive | WA | Extra Large General Service | Time-of-Use Opt-Out | Per Participant Annual Incentive | $/participant/year |  |  |  | Extra Large General ServicePer Participant Annual Incentive | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutPer kW Annual Incentive | WA | Extra Large General Service | Time-of-Use Opt-Out | Per kW Annual Incentive | $/kW @meter/year |  |  |  | Extra Large General ServicePer kW Annual Incentive | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutProgram Development Cost | WA | Extra Large General Service | Time-of-Use Opt-Out | Program Development Cost | $/program |  |  |  | Extra Large General ServiceProgram Development Cost | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutProgram Life | WA | Extra Large General Service | Time-of-Use Opt-Out | Program Life | years |  |  |  | Extra Large General ServiceProgram Life | Market PotentialWA
WAExtra Large General ServiceTime-of-Use Opt-OutProgram Start Year | WA | Extra Large General Service | Time-of-Use Opt-Out | Program Start Year | year |  |  |  | Extra Large General ServiceProgram Start Year | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inSummer DR Event Hours | WA | GS-EV | Electric Vehicle TOU Opt-in | Summer DR Event Hours | hours/year | 528 | Six hours on-peak period each summer weekday |  | GS-EVSummer DR Event Hours | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inWinter DR Event Hours | WA | GS-EV | Electric Vehicle TOU Opt-in | Winter DR Event Hours | hours/year | 528 | Six hours on-peak period each winter weekday too, except for Utah |  | GS-EVWinter DR Event Hours | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inAnnual O&M Cost | WA | GS-EV | Electric Vehicle TOU Opt-in | Annual O&M Cost | $/participant/year | 0 | 0 |  | GS-EVAnnual O&M Cost | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inAnnual O&M Cost per MW | WA | GS-EV | Electric Vehicle TOU Opt-in | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | GS-EVAnnual O&M Cost per MW | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inAnnual Program Administration Cost | WA | GS-EV | Electric Vehicle TOU Opt-in | Annual Program Administration Cost | $/yr | 32916.248 | 0 |  | GS-EVAnnual Program Administration Cost | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inCost of Equip + Install | WA | GS-EV | Electric Vehicle TOU Opt-in | Cost of Equip + Install | $/tech | 0 | 0 |  | GS-EVCost of Equip + Install | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inCost of Equip + Install (per kW basis) | WA | GS-EV | Electric Vehicle TOU Opt-in | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | GS-EVCost of Equip + Install (per kW basis) | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inDe-rate | WA | GS-EV | Electric Vehicle TOU Opt-in | De-rate | capacity equivalence factor | 1 | 0 |  | GS-EVDe-rate | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inNet to Gross Ratio (free ridership) | WA | GS-EV | Electric Vehicle TOU Opt-in | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | GS-EVNet to Gross Ratio (free ridership) | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inPer Customer Annual Marketing/Recruitment Cost | WA | GS-EV | Electric Vehicle TOU Opt-in | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | 2024 Avista Update |  | GS-EVPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inPer Participant Annual Incentive | WA | GS-EV | Electric Vehicle TOU Opt-in | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | GS-EVPer Participant Annual Incentive | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inPer kW Annual Incentive | WA | GS-EV | Electric Vehicle TOU Opt-in | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | GS-EVPer kW Annual Incentive | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inProgram Development Cost | WA | GS-EV | Electric Vehicle TOU Opt-in | Program Development Cost | $/program | 0 | 0 |  | GS-EVProgram Development Cost | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inProgram Life | WA | GS-EV | Electric Vehicle TOU Opt-in | Program Life | years | 10 | 0 |  | GS-EVProgram Life | Market PotentialWA
WAGS-EVElectric Vehicle TOU Opt-inProgram Start Year | WA | GS-EV | Electric Vehicle TOU Opt-in | Program Start Year | year | 2025 | 2024 Avista Update |  | GS-EVProgram Start Year | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inSummer DR Event Hours | WA | LGS-EV | Electric Vehicle TOU Opt-in | Summer DR Event Hours | hours/year | 528 | Six hours on-peak period each summer weekday |  | LGS-EVSummer DR Event Hours | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inWinter DR Event Hours | WA | LGS-EV | Electric Vehicle TOU Opt-in | Winter DR Event Hours | hours/year | 528 | Six hours on-peak period each winter weekday too, except for Utah |  | LGS-EVWinter DR Event Hours | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inAnnual O&M Cost | WA | LGS-EV | Electric Vehicle TOU Opt-in | Annual O&M Cost | $/participant/year | 0 | 0 |  | LGS-EVAnnual O&M Cost | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inAnnual O&M Cost per MW | WA | LGS-EV | Electric Vehicle TOU Opt-in | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | LGS-EVAnnual O&M Cost per MW | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inAnnual Program Administration Cost | WA | LGS-EV | Electric Vehicle TOU Opt-in | Annual Program Administration Cost | $/yr | 12359.2575 | 0 |  | LGS-EVAnnual Program Administration Cost | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inCost of Equip + Install | WA | LGS-EV | Electric Vehicle TOU Opt-in | Cost of Equip + Install | $/tech | 0 | 0 |  | LGS-EVCost of Equip + Install | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inCost of Equip + Install (per kW basis) | WA | LGS-EV | Electric Vehicle TOU Opt-in | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | LGS-EVCost of Equip + Install (per kW basis) | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inDe-rate | WA | LGS-EV | Electric Vehicle TOU Opt-in | De-rate | capacity equivalence factor | 1 | 0 |  | LGS-EVDe-rate | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inNet to Gross Ratio (free ridership) | WA | LGS-EV | Electric Vehicle TOU Opt-in | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | LGS-EVNet to Gross Ratio (free ridership) | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inPer Customer Annual Marketing/Recruitment Cost | WA | LGS-EV | Electric Vehicle TOU Opt-in | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | 2024 Avista Update |  | LGS-EVPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inPer Participant Annual Incentive | WA | LGS-EV | Electric Vehicle TOU Opt-in | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | LGS-EVPer Participant Annual Incentive | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inPer kW Annual Incentive | WA | LGS-EV | Electric Vehicle TOU Opt-in | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | LGS-EVPer kW Annual Incentive | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inProgram Development Cost | WA | LGS-EV | Electric Vehicle TOU Opt-in | Program Development Cost | $/program | 0 | 0 |  | LGS-EVProgram Development Cost | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inProgram Life | WA | LGS-EV | Electric Vehicle TOU Opt-in | Program Life | years | 10 | 0 |  | LGS-EVProgram Life | Market PotentialWA
WALGS-EVElectric Vehicle TOU Opt-inProgram Start Year | WA | LGS-EV | Electric Vehicle TOU Opt-in | Program Start Year | year | 2025 | 2024 Avista Update |  | LGS-EVProgram Start Year | Market PotentialWA
WAResidentialPilot-Peak Time RebateSummer DR Event Hours | WA | Residential | Pilot-Peak Time Rebate | Summer DR Event Hours | hours/year | 40 | 4 hours per event, 15-20 events per year. 3 hours per event in PGE, 5 summer and 2 winter events. |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialPilot-Peak Time RebateWinter DR Event Hours | WA | Residential | Pilot-Peak Time Rebate | Winter DR Event Hours | hours/year | 40 | 4 hours per event, 15-20 events per year. 3 hours per event in PGE, 5 summer and 2 winter events. |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialPilot-Peak Time RebateAnnual O&M Cost | WA | Residential | Pilot-Peak Time Rebate | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialPilot-Peak Time RebateAnnual O&M Cost per MW | WA | Residential | Pilot-Peak Time Rebate | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialPilot-Peak Time RebateAnnual Program Administration Cost | WA | Residential | Pilot-Peak Time Rebate | Annual Program Administration Cost | $/yr | 29934.3594 | 0 |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialPilot-Peak Time RebateCost of Equip + Install | WA | Residential | Pilot-Peak Time Rebate | Cost of Equip + Install | $/tech | 0 | Assume zero, but would be $470 w tech costs included. Based on PacifiCorp estimate: $270 for PCT, plus $200 for installation |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialPilot-Peak Time RebateCost of Equip + Install (per kW basis) | WA | Residential | Pilot-Peak Time Rebate | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialPilot-Peak Time RebateDe-rate | WA | Residential | Pilot-Peak Time Rebate | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialPilot-Peak Time RebateNet to Gross Ratio (free ridership) | WA | Residential | Pilot-Peak Time Rebate | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialPilot-Peak Time RebatePer Customer Annual Marketing/Recruitment Cost | WA | Residential | Pilot-Peak Time Rebate | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | 0 |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialPilot-Peak Time RebatePer Participant Annual Incentive | WA | Residential | Pilot-Peak Time Rebate | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialPilot-Peak Time RebatePer kW Annual Incentive | WA | Residential | Pilot-Peak Time Rebate | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialPilot-Peak Time RebateProgram Development Cost | WA | Residential | Pilot-Peak Time Rebate | Program Development Cost | $/program | 898030.7805 | 0 |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialPilot-Peak Time RebateProgram Life | WA | Residential | Pilot-Peak Time Rebate | Program Life | years | 10 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialPilot-Peak Time RebateProgram Start Year | WA | Residential | Pilot-Peak Time Rebate | Program Start Year | year | 2024 | 0 |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebateSummer DR Event Hours | WA | General Service | Pilot-Peak Time Rebate | Summer DR Event Hours | hours/year | 40 | 4 hours per event, 15-20 events per year |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebateWinter DR Event Hours | WA | General Service | Pilot-Peak Time Rebate | Winter DR Event Hours | hours/year | 40 | 4 hours per event, 15-20 events per year |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebateAnnual O&M Cost | WA | General Service | Pilot-Peak Time Rebate | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebateAnnual O&M Cost per MW | WA | General Service | Pilot-Peak Time Rebate | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebateAnnual Program Administration Cost | WA | General Service | Pilot-Peak Time Rebate | Annual Program Administration Cost | $/yr | 3548.1426 | 0 |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebateCost of Equip + Install | WA | General Service | Pilot-Peak Time Rebate | Cost of Equip + Install | $/tech | 0 | Assume zero, but would be $470 w tech costs included. Based on PacifiCorp estimate: $270 for PCT, plus $200 for installation |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebateCost of Equip + Install (per kW basis) | WA | General Service | Pilot-Peak Time Rebate | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebateDe-rate | WA | General Service | Pilot-Peak Time Rebate | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebateNet to Gross Ratio (free ridership) | WA | General Service | Pilot-Peak Time Rebate | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebatePer Customer Annual Marketing/Recruitment Cost | WA | General Service | Pilot-Peak Time Rebate | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | 0 |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebatePer Participant Annual Incentive | WA | General Service | Pilot-Peak Time Rebate | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebatePer kW Annual Incentive | WA | General Service | Pilot-Peak Time Rebate | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebateProgram Development Cost | WA | General Service | Pilot-Peak Time Rebate | Program Development Cost | $/program | 106444.278 | 0 |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebateProgram Life | WA | General Service | Pilot-Peak Time Rebate | Program Life | years | 10 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServicePilot-Peak Time RebateProgram Start Year | WA | General Service | Pilot-Peak Time Rebate | Program Start Year | year | 2024 | 0 |  | General ServiceProgram Start Year | Market PotentialWA
WAResidentialParent-Peak Time RebateSummer DR Event Hours | WA | Residential | Parent-Peak Time Rebate | Summer DR Event Hours | hours/year | 40 | 4 hours per event, 15-20 events per year. 3 hours per event in PGE, 5 summer and 2 winter events. |  | ResidentialSummer DR Event Hours | Market PotentialWA
WAResidentialParent-Peak Time RebateWinter DR Event Hours | WA | Residential | Parent-Peak Time Rebate | Winter DR Event Hours | hours/year | 40 | 4 hours per event, 15-20 events per year. 3 hours per event in PGE, 5 summer and 2 winter events. |  | ResidentialWinter DR Event Hours | Market PotentialWA
WAResidentialParent-Peak Time RebateAnnual O&M Cost | WA | Residential | Parent-Peak Time Rebate | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialWA
WAResidentialParent-Peak Time RebateAnnual O&M Cost per MW | WA | Residential | Parent-Peak Time Rebate | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialWA
WAResidentialParent-Peak Time RebateAnnual Program Administration Cost | WA | Residential | Parent-Peak Time Rebate | Annual Program Administration Cost | $/yr | 29940.3462 | 0 |  | ResidentialAnnual Program Administration Cost | Market PotentialWA
WAResidentialParent-Peak Time RebateCost of Equip + Install | WA | Residential | Parent-Peak Time Rebate | Cost of Equip + Install | $/tech | 0 | Assume zero, but would be $470 w tech costs included. Based on PacifiCorp estimate: $270 for PCT, plus $200 for installation |  | ResidentialCost of Equip + Install | Market PotentialWA
WAResidentialParent-Peak Time RebateCost of Equip + Install (per kW basis) | WA | Residential | Parent-Peak Time Rebate | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialWA
WAResidentialParent-Peak Time RebateDe-rate | WA | Residential | Parent-Peak Time Rebate | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialWA
WAResidentialParent-Peak Time RebateNet to Gross Ratio (free ridership) | WA | Residential | Parent-Peak Time Rebate | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialWA
WAResidentialParent-Peak Time RebatePer Customer Annual Marketing/Recruitment Cost | WA | Residential | Parent-Peak Time Rebate | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | 2024 Avista Update |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAResidentialParent-Peak Time RebatePer Participant Annual Incentive | WA | Residential | Parent-Peak Time Rebate | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | ResidentialPer Participant Annual Incentive | Market PotentialWA
WAResidentialParent-Peak Time RebatePer kW Annual Incentive | WA | Residential | Parent-Peak Time Rebate | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialWA
WAResidentialParent-Peak Time RebateProgram Development Cost | WA | Residential | Parent-Peak Time Rebate | Program Development Cost | $/program | 898030.7805 | 0 |  | ResidentialProgram Development Cost | Market PotentialWA
WAResidentialParent-Peak Time RebateProgram Life | WA | Residential | Parent-Peak Time Rebate | Program Life | years | 10 | 0 |  | ResidentialProgram Life | Market PotentialWA
WAResidentialParent-Peak Time RebateProgram Start Year | WA | Residential | Parent-Peak Time Rebate | Program Start Year | year | 2025 | 2024 Avista: ID start in 2028 |  | ResidentialProgram Start Year | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebateSummer DR Event Hours | WA | General Service | Parent-Peak Time Rebate | Summer DR Event Hours | hours/year | 40 | 4 hours per event, 15-20 events per year |  | General ServiceSummer DR Event Hours | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebateWinter DR Event Hours | WA | General Service | Parent-Peak Time Rebate | Winter DR Event Hours | hours/year | 40 | 4 hours per event, 15-20 events per year |  | General ServiceWinter DR Event Hours | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebateAnnual O&M Cost | WA | General Service | Parent-Peak Time Rebate | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebateAnnual O&M Cost per MW | WA | General Service | Parent-Peak Time Rebate | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebateAnnual Program Administration Cost | WA | General Service | Parent-Peak Time Rebate | Annual Program Administration Cost | $/yr | 3548.8522 | 0 |  | General ServiceAnnual Program Administration Cost | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebateCost of Equip + Install | WA | General Service | Parent-Peak Time Rebate | Cost of Equip + Install | $/tech | 0 | Assume zero, but would be $470 w tech costs included. Based on PacifiCorp estimate: $270 for PCT, plus $200 for installation |  | General ServiceCost of Equip + Install | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebateCost of Equip + Install (per kW basis) | WA | General Service | Parent-Peak Time Rebate | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebateDe-rate | WA | General Service | Parent-Peak Time Rebate | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebateNet to Gross Ratio (free ridership) | WA | General Service | Parent-Peak Time Rebate | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebatePer Customer Annual Marketing/Recruitment Cost | WA | General Service | Parent-Peak Time Rebate | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | 2024 Avista Update |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebatePer Participant Annual Incentive | WA | General Service | Parent-Peak Time Rebate | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | General ServicePer Participant Annual Incentive | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebatePer kW Annual Incentive | WA | General Service | Parent-Peak Time Rebate | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebateProgram Development Cost | WA | General Service | Parent-Peak Time Rebate | Program Development Cost | $/program | 106444.278 | 0 |  | General ServiceProgram Development Cost | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebateProgram Life | WA | General Service | Parent-Peak Time Rebate | Program Life | years | 10 | 0 |  | General ServiceProgram Life | Market PotentialWA
WAGeneral ServiceParent-Peak Time RebateProgram Start Year | WA | General Service | Parent-Peak Time Rebate | Program Start Year | year | 2025 | 2024 Avista: ID start in 2028 |  | General ServiceProgram Start Year | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesSummer DR Event Hours | WA | Large General Service | Variable Peak Pricing Rates | Summer DR Event Hours | hours/year | 40 | Top 40 summer system hours |  | Large General ServiceSummer DR Event Hours | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesWinter DR Event Hours | WA | Large General Service | Variable Peak Pricing Rates | Winter DR Event Hours | hours/year | 40 | Using summer hours except for UT |  | Large General ServiceWinter DR Event Hours | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesAnnual O&M Cost | WA | Large General Service | Variable Peak Pricing Rates | Annual O&M Cost | $/participant/year | 0 | 0 |  | Large General ServiceAnnual O&M Cost | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesAnnual O&M Cost per MW | WA | Large General Service | Variable Peak Pricing Rates | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | Large General ServiceAnnual O&M Cost per MW | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesAnnual Program Administration Cost | WA | Large General Service | Variable Peak Pricing Rates | Annual Program Administration Cost | $/yr | 39233.2746 | 0 |  | Large General ServiceAnnual Program Administration Cost | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesCost of Equip + Install | WA | Large General Service | Variable Peak Pricing Rates | Cost of Equip + Install | $/tech | 0 | No equipment cost because assuming they have their own technology (like a Energy Management System etc) to control their processes |  | Large General ServiceCost of Equip + Install | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesCost of Equip + Install (per kW basis) | WA | Large General Service | Variable Peak Pricing Rates | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | Currently zero, but $360/kW if tech costs included. Based on Auto-DR tech enablement costs. $300/kW is incentive level offered by SCE for Auto-DR participants, and is expected to cover a large fraction of costs. 20% adder included to recognize some additional expenses on the part of the customer. |  | Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesDe-rate | WA | Large General Service | Variable Peak Pricing Rates | De-rate | capacity equivalence factor | 1 | 0 |  | Large General ServiceDe-rate | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesNet to Gross Ratio (free ridership) | WA | Large General Service | Variable Peak Pricing Rates | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesPer Customer Annual Marketing/Recruitment Cost | WA | Large General Service | Variable Peak Pricing Rates | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 200 | Assumed 4X Residential recruitment costs of $50 |  | Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesPer Participant Annual Incentive | WA | Large General Service | Variable Peak Pricing Rates | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | Large General ServicePer Participant Annual Incentive | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesPer kW Annual Incentive | WA | Large General Service | Variable Peak Pricing Rates | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | Large General ServicePer kW Annual Incentive | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesProgram Development Cost | WA | Large General Service | Variable Peak Pricing Rates | Program Development Cost | $/program | 39233.2746 | 0 |  | Large General ServiceProgram Development Cost | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesProgram Life | WA | Large General Service | Variable Peak Pricing Rates | Program Life | years | 10 | 0 |  | Large General ServiceProgram Life | Market PotentialWA
WALarge General ServiceVariable Peak Pricing RatesProgram Start Year | WA | Large General Service | Variable Peak Pricing Rates | Program Start Year | year | 2026 | Metering capability exists in this class, but need 2 years before program can be implemented and ramp up. |  | Large General ServiceProgram Start Year | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesSummer DR Event Hours | WA | Extra Large General Service | Variable Peak Pricing Rates | Summer DR Event Hours | hours/year | 40 | Top 40 summer system hours |  | Extra Large General ServiceSummer DR Event Hours | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesWinter DR Event Hours | WA | Extra Large General Service | Variable Peak Pricing Rates | Winter DR Event Hours | hours/year | 40 | Using summer hours except for UT |  | Extra Large General ServiceWinter DR Event Hours | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesAnnual O&M Cost | WA | Extra Large General Service | Variable Peak Pricing Rates | Annual O&M Cost | $/participant/year | 0 | 0 |  | Extra Large General ServiceAnnual O&M Cost | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesAnnual O&M Cost per MW | WA | Extra Large General Service | Variable Peak Pricing Rates | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | Extra Large General ServiceAnnual O&M Cost per MW | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesAnnual Program Administration Cost | WA | Extra Large General Service | Variable Peak Pricing Rates | Annual Program Administration Cost | $/yr | 12264.7425 | 0 |  | Extra Large General ServiceAnnual Program Administration Cost | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesCost of Equip + Install | WA | Extra Large General Service | Variable Peak Pricing Rates | Cost of Equip + Install | $/tech | 0 | 0 |  | Extra Large General ServiceCost of Equip + Install | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesCost of Equip + Install (per kW basis) | WA | Extra Large General Service | Variable Peak Pricing Rates | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | Currently zero, but $360/kW if tech costs included. Based on Auto-DR tech enablement costs. $300/kW is incentive level offered by SCE for Auto-DR participants, and is expected to cover a large fraction of costs. 20% adder included to recognize some additional expenses on the part of the customer. |  | Extra Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesDe-rate | WA | Extra Large General Service | Variable Peak Pricing Rates | De-rate | capacity equivalence factor | 1 | 0 |  | Extra Large General ServiceDe-rate | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesNet to Gross Ratio (free ridership) | WA | Extra Large General Service | Variable Peak Pricing Rates | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | Extra Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesPer Customer Annual Marketing/Recruitment Cost | WA | Extra Large General Service | Variable Peak Pricing Rates | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 400 | Assumed 2X Large C&I recruitment costs |  | Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesPer Participant Annual Incentive | WA | Extra Large General Service | Variable Peak Pricing Rates | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | Extra Large General ServicePer Participant Annual Incentive | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesPer kW Annual Incentive | WA | Extra Large General Service | Variable Peak Pricing Rates | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | Extra Large General ServicePer kW Annual Incentive | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesProgram Development Cost | WA | Extra Large General Service | Variable Peak Pricing Rates | Program Development Cost | $/program | 12264.7425 | 0 |  | Extra Large General ServiceProgram Development Cost | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesProgram Life | WA | Extra Large General Service | Variable Peak Pricing Rates | Program Life | years | 10 | 0 |  | Extra Large General ServiceProgram Life | Market PotentialWA
WAExtra Large General ServiceVariable Peak Pricing RatesProgram Start Year | WA | Extra Large General Service | Variable Peak Pricing Rates | Program Start Year | year | 2026 | Metering capability exists in this class, but need 2 years before program can be implemented and ramp up. |  | Extra Large General ServiceProgram Start Year | Market PotentialWA
IDResidentialDLC Central ACSummer DR Event Hours | ID | Residential | DLC Central AC | Summer DR Event Hours | hours/year | 50 | Current PC Cool Keeper program allows for max 100 hours of curtailment. |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialDLC Central ACWinter DR Event Hours | ID | Residential | DLC Central AC | Winter DR Event Hours | hours/year | 0 | 0 |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialDLC Central ACAnnual O&M Cost | ID | Residential | DLC Central AC | Annual O&M Cost | $/participant/year | 13 | Assume 5% of equipment + install costs. |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialDLC Central ACAnnual O&M Cost per MW | ID | Residential | DLC Central AC | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialDLC Central ACAnnual Program Administration Cost | ID | Residential | DLC Central AC | Annual Program Administration Cost | $/yr | 29939.2462 | Share of Cost as noted in table at right |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialDLC Central ACCost of Equip + Install | ID | Residential | DLC Central AC | Cost of Equip + Install | $/tech | 260 | $100 installation cost. Idaho Power at 10,000 quantity pays $160 per switch. It's believed Avista volumes would be the same or less per order, making the cost $160 or greater. |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialDLC Central ACCost of Equip + Install (per kW basis) | ID | Residential | DLC Central AC | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialDLC Central ACDe-rate | ID | Residential | DLC Central AC | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialDLC Central ACNet to Gross Ratio (free ridership) | ID | Residential | DLC Central AC | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialDLC Central ACPer Customer Annual Marketing/Recruitment Cost | ID | Residential | DLC Central AC | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Utah $50, All others $60 (20% higher) |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialDLC Central ACPer Participant Annual Incentive | ID | Residential | DLC Central AC | Per Participant Annual Incentive | $/participant/year | 20 | $20 is the incentive level per participating unit. No. of units per average participant is 1.059. Aligns with ID Power rebate. |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialDLC Central ACPer kW Annual Incentive | ID | Residential | DLC Central AC | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialDLC Central ACProgram Development Cost | ID | Residential | DLC Central AC | Program Development Cost | $/program | 24949.3718 | 0 |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialDLC Central ACProgram Life | ID | Residential | DLC Central AC | Program Life | years | 8 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialDLC Central ACProgram Start Year | ID | Residential | DLC Central AC | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServiceDLC Central ACSummer DR Event Hours | ID | General Service | DLC Central AC | Summer DR Event Hours | hours/year | 50 | Current PC Cool Keeper program allows for max 100 hours of curtailment. |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceDLC Central ACWinter DR Event Hours | ID | General Service | DLC Central AC | Winter DR Event Hours | hours/year | 0 | 0 |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceDLC Central ACAnnual O&M Cost | ID | General Service | DLC Central AC | Annual O&M Cost | $/participant/year | 13 | Assume 5% of equipment + install costs. |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceDLC Central ACAnnual O&M Cost per MW | ID | General Service | DLC Central AC | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceDLC Central ACAnnual Program Administration Cost | ID | General Service | DLC Central AC | Annual Program Administration Cost | $/yr | 3138.2687 | Share of Cost as noted in table at right |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceDLC Central ACCost of Equip + Install | ID | General Service | DLC Central AC | Cost of Equip + Install | $/tech | 260 | $100 installation cost. Idaho Power at 10,000 quantity pays $160 per switch. It's believed Avista volumes would be the same or less per order, making the cost $160 or greater. |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceDLC Central ACCost of Equip + Install (per kW basis) | ID | General Service | DLC Central AC | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceDLC Central ACDe-rate | ID | General Service | DLC Central AC | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceDLC Central ACNet to Gross Ratio (free ridership) | ID | General Service | DLC Central AC | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceDLC Central ACPer Customer Annual Marketing/Recruitment Cost | ID | General Service | DLC Central AC | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | 25% Higher than Residential |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceDLC Central ACPer Participant Annual Incentive | ID | General Service | DLC Central AC | Per Participant Annual Incentive | $/participant/year | 38 | Assumed participants have less than 5.5 tons of AC unit. Incentive level provided by PacifiCorp. |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceDLC Central ACPer kW Annual Incentive | ID | General Service | DLC Central AC | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceDLC Central ACProgram Development Cost | ID | General Service | DLC Central AC | Program Development Cost | $/program | 2615.2239 | 0 |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceDLC Central ACProgram Life | ID | General Service | DLC Central AC | Program Life | years | 8 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceDLC Central ACProgram Start Year | ID | General Service | DLC Central AC | Program Start Year | year | 2026 | 0 |  | General ServiceProgram Start Year | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingSummer DR Event Hours | ID | Residential | DLC Smart Thermostats - Cooling | Summer DR Event Hours | hours/year | 36 | 2016 M&V Report Event Hours |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingWinter DR Event Hours | ID | Residential | DLC Smart Thermostats - Cooling | Winter DR Event Hours | hours/year | 0 | 0 |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingAnnual O&M Cost | ID | Residential | DLC Smart Thermostats - Cooling | Annual O&M Cost | $/participant/year | 164 | 2024 Avista Update: $44 + $10/month fee per tstat |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingAnnual O&M Cost per MW | ID | Residential | DLC Smart Thermostats - Cooling | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingAnnual Program Administration Cost | ID | Residential | DLC Smart Thermostats - Cooling | Annual Program Administration Cost | $/yr | 29939.2462 | 0 |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingCost of Equip + Install | ID | Residential | DLC Smart Thermostats - Cooling | Cost of Equip + Install | $/tech | 0 | Bring Your Own Thermostat program |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingCost of Equip + Install (per kW basis) | ID | Residential | DLC Smart Thermostats - Cooling | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingDe-rate | ID | Residential | DLC Smart Thermostats - Cooling | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingNet to Gross Ratio (free ridership) | ID | Residential | DLC Smart Thermostats - Cooling | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingPer Customer Annual Marketing/Recruitment Cost | ID | Residential | DLC Smart Thermostats - Cooling | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Utah $50, All others $60 (20% higher) |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingPer Participant Annual Incentive | ID | Residential | DLC Smart Thermostats - Cooling | Per Participant Annual Incentive | $/participant/year | 20 | Assume $20 per year per system, same as CAC DLC. |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingPer kW Annual Incentive | ID | Residential | DLC Smart Thermostats - Cooling | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingProgram Development Cost | ID | Residential | DLC Smart Thermostats - Cooling | Program Development Cost | $/program | 116430.4017 | Share of Cost as noted in table at right |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingProgram Life | ID | Residential | DLC Smart Thermostats - Cooling | Program Life | years | 10 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialDLC Smart Thermostats - CoolingProgram Start Year | ID | Residential | DLC Smart Thermostats - Cooling | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingSummer DR Event Hours | ID | General Service | DLC Smart Thermostats - Cooling | Summer DR Event Hours | hours/year | 36 | 2016 M&V Report Event Hours |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingWinter DR Event Hours | ID | General Service | DLC Smart Thermostats - Cooling | Winter DR Event Hours | hours/year | 0 | 0 |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingAnnual O&M Cost | ID | General Service | DLC Smart Thermostats - Cooling | Annual O&M Cost | $/participant/year | 164 | 2024 Avista Update: $44 + $10/month fee per tstat |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingAnnual O&M Cost per MW | ID | General Service | DLC Smart Thermostats - Cooling | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingAnnual Program Administration Cost | ID | General Service | DLC Smart Thermostats - Cooling | Annual Program Administration Cost | $/yr | 3138.2687 | 0 |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingCost of Equip + Install | ID | General Service | DLC Smart Thermostats - Cooling | Cost of Equip + Install | $/tech | 0 | Bring Your Own Thermostat program |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingCost of Equip + Install (per kW basis) | ID | General Service | DLC Smart Thermostats - Cooling | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingDe-rate | ID | General Service | DLC Smart Thermostats - Cooling | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingNet to Gross Ratio (free ridership) | ID | General Service | DLC Smart Thermostats - Cooling | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingPer Customer Annual Marketing/Recruitment Cost | ID | General Service | DLC Smart Thermostats - Cooling | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | Utah $50, All others $60 (25% higher) |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingPer Participant Annual Incentive | ID | General Service | DLC Smart Thermostats - Cooling | Per Participant Annual Incentive | $/participant/year | 20 | Assume $20 per year per system, same as CAC DLC. |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingPer kW Annual Incentive | ID | General Service | DLC Smart Thermostats - Cooling | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingProgram Development Cost | ID | General Service | DLC Smart Thermostats - Cooling | Program Development Cost | $/program | 12204.3782 | Share of Cost as noted in table at right |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingProgram Life | ID | General Service | DLC Smart Thermostats - Cooling | Program Life | years | 10 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - CoolingProgram Start Year | ID | General Service | DLC Smart Thermostats - Cooling | Program Start Year | year | 2026 | 0 |  | General ServiceProgram Start Year | Market PotentialID
IDResidentialAncillary CoolingSummer DR Event Hours | ID | Residential | Ancillary Cooling | Summer DR Event Hours | hours/year | 36 | 2016 M&V Report Event Hours |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialAncillary CoolingWinter DR Event Hours | ID | Residential | Ancillary Cooling | Winter DR Event Hours | hours/year | 0 | 0 |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialAncillary CoolingAnnual O&M Cost | ID | Residential | Ancillary Cooling | Annual O&M Cost | $/participant/year | 0 | Zero for Ancillary |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialAncillary CoolingAnnual O&M Cost per MW | ID | Residential | Ancillary Cooling | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialAncillary CoolingAnnual Program Administration Cost | ID | Residential | Ancillary Cooling | Annual Program Administration Cost | $/yr | 9979.7487 | Half for Ancillary- tied to participation reduction from parent program |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialAncillary CoolingCost of Equip + Install | ID | Residential | Ancillary Cooling | Cost of Equip + Install | $/tech | 0 | BYOT |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialAncillary CoolingCost of Equip + Install (per kW basis) | ID | Residential | Ancillary Cooling | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialAncillary CoolingDe-rate | ID | Residential | Ancillary Cooling | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialAncillary CoolingNet to Gross Ratio (free ridership) | ID | Residential | Ancillary Cooling | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialAncillary CoolingPer Customer Annual Marketing/Recruitment Cost | ID | Residential | Ancillary Cooling | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Utah $50, All others $60 (20% higher) |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialAncillary CoolingPer Participant Annual Incentive | ID | Residential | Ancillary Cooling | Per Participant Annual Incentive | $/participant/year | 20 | Assume $20 per year per system, same as CAC DLC. Adding $20 to account for ancillary service option |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialAncillary CoolingPer kW Annual Incentive | ID | Residential | Ancillary Cooling | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialAncillary CoolingProgram Development Cost | ID | Residential | Ancillary Cooling | Program Development Cost | $/program | 12474.6859 | Half for Ancillary- tied to participation reduction from parent program |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialAncillary CoolingProgram Life | ID | Residential | Ancillary Cooling | Program Life | years | 10 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialAncillary CoolingProgram Start Year | ID | Residential | Ancillary Cooling | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServiceAncillary CoolingSummer DR Event Hours | ID | General Service | Ancillary Cooling | Summer DR Event Hours | hours/year | 36 | 2016 M&V Report Event Hours |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceAncillary CoolingWinter DR Event Hours | ID | General Service | Ancillary Cooling | Winter DR Event Hours | hours/year | 0 | 0 |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceAncillary CoolingAnnual O&M Cost | ID | General Service | Ancillary Cooling | Annual O&M Cost | $/participant/year | 0 | Zero since part of parent program |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceAncillary CoolingAnnual O&M Cost per MW | ID | General Service | Ancillary Cooling | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceAncillary CoolingAnnual Program Administration Cost | ID | General Service | Ancillary Cooling | Annual Program Administration Cost | $/yr | 1046.0896 | Half for Ancillary- tied to participation reduction from parent program |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceAncillary CoolingCost of Equip + Install | ID | General Service | Ancillary Cooling | Cost of Equip + Install | $/tech | 0 | Bring Your Own Thermostat program |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceAncillary CoolingCost of Equip + Install (per kW basis) | ID | General Service | Ancillary Cooling | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceAncillary CoolingDe-rate | ID | General Service | Ancillary Cooling | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceAncillary CoolingNet to Gross Ratio (free ridership) | ID | General Service | Ancillary Cooling | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceAncillary CoolingPer Customer Annual Marketing/Recruitment Cost | ID | General Service | Ancillary Cooling | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | Utah $50, All others $60 (25% higher) |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceAncillary CoolingPer Participant Annual Incentive | ID | General Service | Ancillary Cooling | Per Participant Annual Incentive | $/participant/year | 20 | Assume $20 per year per system, same as CAC DLC. Adding $20 to account for ancillary service option |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceAncillary CoolingPer kW Annual Incentive | ID | General Service | Ancillary Cooling | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceAncillary CoolingProgram Development Cost | ID | General Service | Ancillary Cooling | Program Development Cost | $/program | 1307.612 | Half for Ancillary- tied to participation reduction from parent program |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceAncillary CoolingProgram Life | ID | General Service | Ancillary Cooling | Program Life | years | 10 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceAncillary CoolingProgram Start Year | ID | General Service | Ancillary Cooling | Program Start Year | year | 2026 | 0 |  | General ServiceProgram Start Year | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingSummer DR Event Hours | ID | Residential | DLC Smart Thermostats - Heating | Summer DR Event Hours | hours/year | 0 | 0 |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingWinter DR Event Hours | ID | Residential | DLC Smart Thermostats - Heating | Winter DR Event Hours | hours/year | 36 | 2016 M&V Report Event Hours |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingAnnual O&M Cost | ID | Residential | DLC Smart Thermostats - Heating | Annual O&M Cost | $/participant/year | 0 | Program would piggy-back off of Thermostats-Cooling and share those costs |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingAnnual O&M Cost per MW | ID | Residential | DLC Smart Thermostats - Heating | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingAnnual Program Administration Cost | ID | Residential | DLC Smart Thermostats - Heating | Annual Program Administration Cost | $/yr | 0 | Program would piggy-back off of Thermostats-Cooling and share those costs |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingCost of Equip + Install | ID | Residential | DLC Smart Thermostats - Heating | Cost of Equip + Install | $/tech | 0 | Bring your own thermostat program |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingCost of Equip + Install (per kW basis) | ID | Residential | DLC Smart Thermostats - Heating | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingDe-rate | ID | Residential | DLC Smart Thermostats - Heating | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingNet to Gross Ratio (free ridership) | ID | Residential | DLC Smart Thermostats - Heating | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingPer Customer Annual Marketing/Recruitment Cost | ID | Residential | DLC Smart Thermostats - Heating | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Utah $50, All others $60 (20% higher) |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingPer Participant Annual Incentive | ID | Residential | DLC Smart Thermostats - Heating | Per Participant Annual Incentive | $/participant/year | 20 | Assume $20 per year per system, same as CAC DLC. |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingPer kW Annual Incentive | ID | Residential | DLC Smart Thermostats - Heating | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingProgram Development Cost | ID | Residential | DLC Smart Thermostats - Heating | Program Development Cost | $/program | 0 | Program would piggy-back off of Thermostats-Cooling and share those costs |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingProgram Life | ID | Residential | DLC Smart Thermostats - Heating | Program Life | years | 10 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialDLC Smart Thermostats - HeatingProgram Start Year | ID | Residential | DLC Smart Thermostats - Heating | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingSummer DR Event Hours | ID | General Service | DLC Smart Thermostats - Heating | Summer DR Event Hours | hours/year | 0 | 0 |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingWinter DR Event Hours | ID | General Service | DLC Smart Thermostats - Heating | Winter DR Event Hours | hours/year | 36 | 2016 M&V Report Event Hours |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingAnnual O&M Cost | ID | General Service | DLC Smart Thermostats - Heating | Annual O&M Cost | $/participant/year | 0 | Program would piggy-back off of Thermostats-Cooling and share those costs |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingAnnual O&M Cost per MW | ID | General Service | DLC Smart Thermostats - Heating | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingAnnual Program Administration Cost | ID | General Service | DLC Smart Thermostats - Heating | Annual Program Administration Cost | $/yr | 0 | Program would piggy-back off of Thermostats-Cooling and share those costs |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingCost of Equip + Install | ID | General Service | DLC Smart Thermostats - Heating | Cost of Equip + Install | $/tech | 0 | Bring your own thermostat program |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingCost of Equip + Install (per kW basis) | ID | General Service | DLC Smart Thermostats - Heating | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingDe-rate | ID | General Service | DLC Smart Thermostats - Heating | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingNet to Gross Ratio (free ridership) | ID | General Service | DLC Smart Thermostats - Heating | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingPer Customer Annual Marketing/Recruitment Cost | ID | General Service | DLC Smart Thermostats - Heating | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | Utah $50, All others $60 (25% higher) |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingPer Participant Annual Incentive | ID | General Service | DLC Smart Thermostats - Heating | Per Participant Annual Incentive | $/participant/year | 20 | Assume $20 per year per system, same as CAC DLC. |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingPer kW Annual Incentive | ID | General Service | DLC Smart Thermostats - Heating | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingProgram Development Cost | ID | General Service | DLC Smart Thermostats - Heating | Program Development Cost | $/program | 0 | Program would piggy-back off of Thermostats-Cooling and share those costs |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingProgram Life | ID | General Service | DLC Smart Thermostats - Heating | Program Life | years | 10 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceDLC Smart Thermostats - HeatingProgram Start Year | ID | General Service | DLC Smart Thermostats - Heating | Program Start Year | year | 2026 | 0 |  | General ServiceProgram Start Year | Market PotentialID
IDResidentialAncillary HeatingSummer DR Event Hours | ID | Residential | Ancillary Heating | Summer DR Event Hours | hours/year | 0 | 0 |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialAncillary HeatingWinter DR Event Hours | ID | Residential | Ancillary Heating | Winter DR Event Hours | hours/year | 36 | 2016 M&V Report Event Hours |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialAncillary HeatingAnnual O&M Cost | ID | Residential | Ancillary Heating | Annual O&M Cost | $/participant/year | 0 | Zero for Ancillary |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialAncillary HeatingAnnual O&M Cost per MW | ID | Residential | Ancillary Heating | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialAncillary HeatingAnnual Program Administration Cost | ID | Residential | Ancillary Heating | Annual Program Administration Cost | $/yr | 0 | Program would piggy-back off of Ancillary-Cooling and share those costs |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialAncillary HeatingCost of Equip + Install | ID | Residential | Ancillary Heating | Cost of Equip + Install | $/tech | 0 | Bring your own thermostat program |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialAncillary HeatingCost of Equip + Install (per kW basis) | ID | Residential | Ancillary Heating | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialAncillary HeatingDe-rate | ID | Residential | Ancillary Heating | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialAncillary HeatingNet to Gross Ratio (free ridership) | ID | Residential | Ancillary Heating | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialAncillary HeatingPer Customer Annual Marketing/Recruitment Cost | ID | Residential | Ancillary Heating | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Utah $50, All others $60 (20% higher) |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialAncillary HeatingPer Participant Annual Incentive | ID | Residential | Ancillary Heating | Per Participant Annual Incentive | $/participant/year | 20 | Assume $20 per year per system, same as CAC DLC. |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialAncillary HeatingPer kW Annual Incentive | ID | Residential | Ancillary Heating | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialAncillary HeatingProgram Development Cost | ID | Residential | Ancillary Heating | Program Development Cost | $/program | 0 | Program would piggy-back off of Ancillary-Cooling and share those costs |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialAncillary HeatingProgram Life | ID | Residential | Ancillary Heating | Program Life | years | 10 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialAncillary HeatingProgram Start Year | ID | Residential | Ancillary Heating | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServiceAncillary HeatingSummer DR Event Hours | ID | General Service | Ancillary Heating | Summer DR Event Hours | hours/year | 0 | 0 |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceAncillary HeatingWinter DR Event Hours | ID | General Service | Ancillary Heating | Winter DR Event Hours | hours/year | 36 | 2016 M&V Report Event Hours |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceAncillary HeatingAnnual O&M Cost | ID | General Service | Ancillary Heating | Annual O&M Cost | $/participant/year | 0 | Zero for Ancillary |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceAncillary HeatingAnnual O&M Cost per MW | ID | General Service | Ancillary Heating | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceAncillary HeatingAnnual Program Administration Cost | ID | General Service | Ancillary Heating | Annual Program Administration Cost | $/yr | 0 | Program would piggy-back off of Ancillary-Cooling and share those costs |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceAncillary HeatingCost of Equip + Install | ID | General Service | Ancillary Heating | Cost of Equip + Install | $/tech | 0 | Bring your own thermostat program |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceAncillary HeatingCost of Equip + Install (per kW basis) | ID | General Service | Ancillary Heating | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceAncillary HeatingDe-rate | ID | General Service | Ancillary Heating | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceAncillary HeatingNet to Gross Ratio (free ridership) | ID | General Service | Ancillary Heating | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceAncillary HeatingPer Customer Annual Marketing/Recruitment Cost | ID | General Service | Ancillary Heating | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | Utah $50, All others $60 (25% higher) |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceAncillary HeatingPer Participant Annual Incentive | ID | General Service | Ancillary Heating | Per Participant Annual Incentive | $/participant/year | 20 | Assume $20 per year per system, same as CAC DLC. |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceAncillary HeatingPer kW Annual Incentive | ID | General Service | Ancillary Heating | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceAncillary HeatingProgram Development Cost | ID | General Service | Ancillary Heating | Program Development Cost | $/program | 0 | Program would piggy-back off of Ancillary-Cooling and share those costs |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceAncillary HeatingProgram Life | ID | General Service | Ancillary Heating | Program Life | years | 10 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceAncillary HeatingProgram Start Year | ID | General Service | Ancillary Heating | Program Start Year | year | 2026 | 0 |  | General ServiceProgram Start Year | Market PotentialID
IDResidentialDLC Water HeatingSummer DR Event Hours | ID | Residential | DLC Water Heating | Summer DR Event Hours | hours/year | 0 | Current PC Cool Keeper CAC DLC program allows for max 100 hours of curtailment. |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialDLC Water HeatingWinter DR Event Hours | ID | Residential | DLC Water Heating | Winter DR Event Hours | hours/year | 50 | Split 50 hrs summer, and 50 hrs winter |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialDLC Water HeatingAnnual O&M Cost | ID | Residential | DLC Water Heating | Annual O&M Cost | $/participant/year | 23 | Assume 5% of equipment + install costs. |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialDLC Water HeatingAnnual O&M Cost per MW | ID | Residential | DLC Water Heating | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialDLC Water HeatingAnnual Program Administration Cost | ID | Residential | DLC Water Heating | Annual Program Administration Cost | $/yr | 81264.0073 | Share of Cost as noted in table at right |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialDLC Water HeatingCost of Equip + Install | ID | Residential | DLC Water Heating | Cost of Equip + Install | $/tech | 460 | Assumed $160 cost for water heater switch (same as cooling switch cost), plus $200 installation cost. Cost of Permit and License is $100 for res and $125 for C&I |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialDLC Water HeatingCost of Equip + Install (per kW basis) | ID | Residential | DLC Water Heating | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialDLC Water HeatingDe-rate | ID | Residential | DLC Water Heating | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialDLC Water HeatingNet to Gross Ratio (free ridership) | ID | Residential | DLC Water Heating | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialDLC Water HeatingPer Customer Annual Marketing/Recruitment Cost | ID | Residential | DLC Water Heating | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Same as DLC CAC |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialDLC Water HeatingPer Participant Annual Incentive | ID | Residential | DLC Water Heating | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialDLC Water HeatingPer kW Annual Incentive | ID | Residential | DLC Water Heating | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialDLC Water HeatingProgram Development Cost | ID | Residential | DLC Water Heating | Program Development Cost | $/program | 67720.0061 | 0 |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialDLC Water HeatingProgram Life | ID | Residential | DLC Water Heating | Program Life | years | 8 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialDLC Water HeatingProgram Start Year | ID | Residential | DLC Water Heating | Program Start Year | year | 2026 | Existing programs in UT. Other states need 2 years to ramp up. |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServiceDLC Water HeatingSummer DR Event Hours | ID | General Service | DLC Water Heating | Summer DR Event Hours | hours/year | 0 | Current PC Cool Keeper CAC DLC program allows for max 100 hours of curtailment. |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceDLC Water HeatingWinter DR Event Hours | ID | General Service | DLC Water Heating | Winter DR Event Hours | hours/year | 50 | Split 50 hrs summer, and 50 hrs winter |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceDLC Water HeatingAnnual O&M Cost | ID | General Service | DLC Water Heating | Annual O&M Cost | $/participant/year | 24.25 | Assume 5% of equipment + install costs. |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceDLC Water HeatingAnnual O&M Cost per MW | ID | General Service | DLC Water Heating | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceDLC Water HeatingAnnual Program Administration Cost | ID | General Service | DLC Water Heating | Annual Program Administration Cost | $/yr | 8735.9927 | Share of Cost as noted in table at right |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceDLC Water HeatingCost of Equip + Install | ID | General Service | DLC Water Heating | Cost of Equip + Install | $/tech | 485 | Assumed $160 cost for water heater switch (same as cooling switch cost), plus $200 installation cost. Cost of Permit and License is $100 for res and $125 for C&I |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceDLC Water HeatingCost of Equip + Install (per kW basis) | ID | General Service | DLC Water Heating | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceDLC Water HeatingDe-rate | ID | General Service | DLC Water Heating | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceDLC Water HeatingNet to Gross Ratio (free ridership) | ID | General Service | DLC Water Heating | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceDLC Water HeatingPer Customer Annual Marketing/Recruitment Cost | ID | General Service | DLC Water Heating | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | Same as DLC CAC |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceDLC Water HeatingPer Participant Annual Incentive | ID | General Service | DLC Water Heating | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceDLC Water HeatingPer kW Annual Incentive | ID | General Service | DLC Water Heating | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceDLC Water HeatingProgram Development Cost | ID | General Service | DLC Water Heating | Program Development Cost | $/program | 7279.9939 | No startup costs; Framework already exists for current programs |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceDLC Water HeatingProgram Life | ID | General Service | DLC Water Heating | Program Life | years | 8 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceDLC Water HeatingProgram Start Year | ID | General Service | DLC Water Heating | Program Start Year | year | 2026 | Existing programs in UT. Other states need 2 years to ramp up. |  | General ServiceProgram Start Year | Market PotentialID
IDResidentialAncillary DLC WHSummer DR Event Hours | ID | Residential | Ancillary DLC WH | Summer DR Event Hours | hours/year | 0 | Current PC Cool Keeper CAC DLC program allows for max 100 hours of curtailment. |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialAncillary DLC WHWinter DR Event Hours | ID | Residential | Ancillary DLC WH | Winter DR Event Hours | hours/year | 50 | Split 50 hrs summer, and 50 hrs winter |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialAncillary DLC WHAnnual O&M Cost | ID | Residential | Ancillary DLC WH | Annual O&M Cost | $/participant/year | 0 | Zero for Ancillary |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialAncillary DLC WHAnnual O&M Cost per MW | ID | Residential | Ancillary DLC WH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialAncillary DLC WHAnnual Program Administration Cost | ID | Residential | Ancillary DLC WH | Annual Program Administration Cost | $/yr | 54176.0049 | Share of Cost as noted in table at right |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialAncillary DLC WHCost of Equip + Install | ID | Residential | Ancillary DLC WH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialAncillary DLC WHCost of Equip + Install (per kW basis) | ID | Residential | Ancillary DLC WH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialAncillary DLC WHDe-rate | ID | Residential | Ancillary DLC WH | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialAncillary DLC WHNet to Gross Ratio (free ridership) | ID | Residential | Ancillary DLC WH | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialAncillary DLC WHPer Customer Annual Marketing/Recruitment Cost | ID | Residential | Ancillary DLC WH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | Same as DLC CAC |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialAncillary DLC WHPer Participant Annual Incentive | ID | Residential | Ancillary DLC WH | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialAncillary DLC WHPer kW Annual Incentive | ID | Residential | Ancillary DLC WH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialAncillary DLC WHProgram Development Cost | ID | Residential | Ancillary DLC WH | Program Development Cost | $/program | 67720.0061 | 0 |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialAncillary DLC WHProgram Life | ID | Residential | Ancillary DLC WH | Program Life | years | 8 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialAncillary DLC WHProgram Start Year | ID | Residential | Ancillary DLC WH | Program Start Year | year | 2026 | Existing programs in UT. Other states need 2 years to ramp up. |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServiceAncillary DLC WHSummer DR Event Hours | ID | General Service | Ancillary DLC WH | Summer DR Event Hours | hours/year | 0 | Current PC Cool Keeper CAC DLC program allows for max 100 hours of curtailment. |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceAncillary DLC WHWinter DR Event Hours | ID | General Service | Ancillary DLC WH | Winter DR Event Hours | hours/year | 0 | Split 50 hrs summer, and 50 hrs winter |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceAncillary DLC WHAnnual O&M Cost | ID | General Service | Ancillary DLC WH | Annual O&M Cost | $/participant/year | 0 | Zero for Ancillary |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceAncillary DLC WHAnnual O&M Cost per MW | ID | General Service | Ancillary DLC WH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceAncillary DLC WHAnnual Program Administration Cost | ID | General Service | Ancillary DLC WH | Annual Program Administration Cost | $/yr | 5823.9951 | Share of Cost as noted in table at right |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceAncillary DLC WHCost of Equip + Install | ID | General Service | Ancillary DLC WH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceAncillary DLC WHCost of Equip + Install (per kW basis) | ID | General Service | Ancillary DLC WH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceAncillary DLC WHDe-rate | ID | General Service | Ancillary DLC WH | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceAncillary DLC WHNet to Gross Ratio (free ridership) | ID | General Service | Ancillary DLC WH | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceAncillary DLC WHPer Customer Annual Marketing/Recruitment Cost | ID | General Service | Ancillary DLC WH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 75 | Same as DLC CAC |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceAncillary DLC WHPer Participant Annual Incentive | ID | General Service | Ancillary DLC WH | Per Participant Annual Incentive | $/participant/year | 24 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceAncillary DLC WHPer kW Annual Incentive | ID | General Service | Ancillary DLC WH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceAncillary DLC WHProgram Development Cost | ID | General Service | Ancillary DLC WH | Program Development Cost | $/program | 7279.9939 | No startup costs; Framework already exists for current programs |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceAncillary DLC WHProgram Life | ID | General Service | Ancillary DLC WH | Program Life | years | 8 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceAncillary DLC WHProgram Start Year | ID | General Service | Ancillary DLC WH | Program Start Year | year | 2026 | Existing programs in UT. Other states need 2 years to ramp up. |  | General ServiceProgram Start Year | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHSummer DR Event Hours | ID | Residential | Pilot-CTA-2045 HPWH | Summer DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHWinter DR Event Hours | ID | Residential | Pilot-CTA-2045 HPWH | Winter DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHAnnual O&M Cost | ID | Residential | Pilot-CTA-2045 HPWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHAnnual O&M Cost per MW | ID | Residential | Pilot-CTA-2045 HPWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHAnnual Program Administration Cost | ID | Residential | Pilot-CTA-2045 HPWH | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHCost of Equip + Install | ID | Residential | Pilot-CTA-2045 HPWH | Cost of Equip + Install | $/tech | 0 | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 for these customers)- average customer will be $170 |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHCost of Equip + Install (per kW basis) | ID | Residential | Pilot-CTA-2045 HPWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHDe-rate | ID | Residential | Pilot-CTA-2045 HPWH | De-rate | capacity equivalence factor | 0 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHNet to Gross Ratio (free ridership) | ID | Residential | Pilot-CTA-2045 HPWH | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHPer Customer Annual Marketing/Recruitment Cost | ID | Residential | Pilot-CTA-2045 HPWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as Smart Thermostats |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHPer Participant Annual Incentive | ID | Residential | Pilot-CTA-2045 HPWH | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHPer kW Annual Incentive | ID | Residential | Pilot-CTA-2045 HPWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHProgram Development Cost | ID | Residential | Pilot-CTA-2045 HPWH | Program Development Cost | $/program | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHProgram Life | ID | Residential | Pilot-CTA-2045 HPWH | Program Life | years | 0 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialPilot-CTA-2045 HPWHProgram Start Year | ID | Residential | Pilot-CTA-2045 HPWH | Program Start Year | year | 0 | 0 |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHSummer DR Event Hours | ID | General Service | Pilot-CTA-2045 HPWH | Summer DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHWinter DR Event Hours | ID | General Service | Pilot-CTA-2045 HPWH | Winter DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHAnnual O&M Cost | ID | General Service | Pilot-CTA-2045 HPWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHAnnual O&M Cost per MW | ID | General Service | Pilot-CTA-2045 HPWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHAnnual Program Administration Cost | ID | General Service | Pilot-CTA-2045 HPWH | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHCost of Equip + Install | ID | General Service | Pilot-CTA-2045 HPWH | Cost of Equip + Install | $/tech | 0 | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 install cost for these customers)- average customer will be $170 |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHCost of Equip + Install (per kW basis) | ID | General Service | Pilot-CTA-2045 HPWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHDe-rate | ID | General Service | Pilot-CTA-2045 HPWH | De-rate | capacity equivalence factor | 0 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHNet to Gross Ratio (free ridership) | ID | General Service | Pilot-CTA-2045 HPWH | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHPer Customer Annual Marketing/Recruitment Cost | ID | General Service | Pilot-CTA-2045 HPWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as Smart Thermostats |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHPer Participant Annual Incentive | ID | General Service | Pilot-CTA-2045 HPWH | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHPer kW Annual Incentive | ID | General Service | Pilot-CTA-2045 HPWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHProgram Development Cost | ID | General Service | Pilot-CTA-2045 HPWH | Program Development Cost | $/program | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHProgram Life | ID | General Service | Pilot-CTA-2045 HPWH | Program Life | years | 0 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServicePilot-CTA-2045 HPWHProgram Start Year | ID | General Service | Pilot-CTA-2045 HPWH | Program Start Year | year | 0 | 0 |  | General ServiceProgram Start Year | Market PotentialID
IDResidentialParent-CTA-2045 HPWHSummer DR Event Hours | ID | Residential | Parent-CTA-2045 HPWH | Summer DR Event Hours | hours/year | 0 | 2024 Avista Update: 70 events each season, 3 hours each |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialParent-CTA-2045 HPWHWinter DR Event Hours | ID | Residential | Parent-CTA-2045 HPWH | Winter DR Event Hours | hours/year | 0 | 2024 Avista Update: 70 events each season, 3 hours each |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialParent-CTA-2045 HPWHAnnual O&M Cost | ID | Residential | Parent-CTA-2045 HPWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialParent-CTA-2045 HPWHAnnual O&M Cost per MW | ID | Residential | Parent-CTA-2045 HPWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialParent-CTA-2045 HPWHAnnual Program Administration Cost | ID | Residential | Parent-CTA-2045 HPWH | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialParent-CTA-2045 HPWHCost of Equip + Install | ID | Residential | Parent-CTA-2045 HPWH | Cost of Equip + Install | $/tech | 0 | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 for these customers)- average customer will be $170 |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialParent-CTA-2045 HPWHCost of Equip + Install (per kW basis) | ID | Residential | Parent-CTA-2045 HPWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialParent-CTA-2045 HPWHDe-rate | ID | Residential | Parent-CTA-2045 HPWH | De-rate | capacity equivalence factor | 0 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialParent-CTA-2045 HPWHNet to Gross Ratio (free ridership) | ID | Residential | Parent-CTA-2045 HPWH | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialParent-CTA-2045 HPWHPer Customer Annual Marketing/Recruitment Cost | ID | Residential | Parent-CTA-2045 HPWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as Smart Thermostats |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialParent-CTA-2045 HPWHPer Participant Annual Incentive | ID | Residential | Parent-CTA-2045 HPWH | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialParent-CTA-2045 HPWHPer kW Annual Incentive | ID | Residential | Parent-CTA-2045 HPWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialParent-CTA-2045 HPWHProgram Development Cost | ID | Residential | Parent-CTA-2045 HPWH | Program Development Cost | $/program | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialParent-CTA-2045 HPWHProgram Life | ID | Residential | Parent-CTA-2045 HPWH | Program Life | years | 0 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialParent-CTA-2045 HPWHProgram Start Year | ID | Residential | Parent-CTA-2045 HPWH | Program Start Year | year | 0 | 0 |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHSummer DR Event Hours | ID | General Service | Parent-CTA-2045 HPWH | Summer DR Event Hours | hours/year | 0 | 2024 Avista Update: 70 events each season, 3 hours each |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHWinter DR Event Hours | ID | General Service | Parent-CTA-2045 HPWH | Winter DR Event Hours | hours/year | 0 | 2024 Avista Update: 70 events each season, 3 hours each |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHAnnual O&M Cost | ID | General Service | Parent-CTA-2045 HPWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHAnnual O&M Cost per MW | ID | General Service | Parent-CTA-2045 HPWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHAnnual Program Administration Cost | ID | General Service | Parent-CTA-2045 HPWH | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHCost of Equip + Install | ID | General Service | Parent-CTA-2045 HPWH | Cost of Equip + Install | $/tech | 0 | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 install cost for these customers)- average customer will be $170 |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHCost of Equip + Install (per kW basis) | ID | General Service | Parent-CTA-2045 HPWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHDe-rate | ID | General Service | Parent-CTA-2045 HPWH | De-rate | capacity equivalence factor | 0 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHNet to Gross Ratio (free ridership) | ID | General Service | Parent-CTA-2045 HPWH | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHPer Customer Annual Marketing/Recruitment Cost | ID | General Service | Parent-CTA-2045 HPWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as Smart Thermostats |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHPer Participant Annual Incentive | ID | General Service | Parent-CTA-2045 HPWH | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHPer kW Annual Incentive | ID | General Service | Parent-CTA-2045 HPWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHProgram Development Cost | ID | General Service | Parent-CTA-2045 HPWH | Program Development Cost | $/program | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHProgram Life | ID | General Service | Parent-CTA-2045 HPWH | Program Life | years | 0 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceParent-CTA-2045 HPWHProgram Start Year | ID | General Service | Parent-CTA-2045 HPWH | Program Start Year | year | 0 | 0 |  | General ServiceProgram Start Year | Market PotentialID
IDResidentialPilot-Ancillary HPWHSummer DR Event Hours | ID | Residential | Pilot-Ancillary HPWH | Summer DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialPilot-Ancillary HPWHWinter DR Event Hours | ID | Residential | Pilot-Ancillary HPWH | Winter DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialPilot-Ancillary HPWHAnnual O&M Cost | ID | Residential | Pilot-Ancillary HPWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialPilot-Ancillary HPWHAnnual O&M Cost per MW | ID | Residential | Pilot-Ancillary HPWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialPilot-Ancillary HPWHAnnual Program Administration Cost | ID | Residential | Pilot-Ancillary HPWH | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialPilot-Ancillary HPWHCost of Equip + Install | ID | Residential | Pilot-Ancillary HPWH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialPilot-Ancillary HPWHCost of Equip + Install (per kW basis) | ID | Residential | Pilot-Ancillary HPWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialPilot-Ancillary HPWHDe-rate | ID | Residential | Pilot-Ancillary HPWH | De-rate | capacity equivalence factor | 0 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialPilot-Ancillary HPWHNet to Gross Ratio (free ridership) | ID | Residential | Pilot-Ancillary HPWH | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialPilot-Ancillary HPWHPer Customer Annual Marketing/Recruitment Cost | ID | Residential | Pilot-Ancillary HPWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as Smart Thermostats |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialPilot-Ancillary HPWHPer Participant Annual Incentive | ID | Residential | Pilot-Ancillary HPWH | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialPilot-Ancillary HPWHPer kW Annual Incentive | ID | Residential | Pilot-Ancillary HPWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialPilot-Ancillary HPWHProgram Development Cost | ID | Residential | Pilot-Ancillary HPWH | Program Development Cost | $/program | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialPilot-Ancillary HPWHProgram Life | ID | Residential | Pilot-Ancillary HPWH | Program Life | years | 0 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialPilot-Ancillary HPWHProgram Start Year | ID | Residential | Pilot-Ancillary HPWH | Program Start Year | year | 0 | 0 |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHSummer DR Event Hours | ID | General Service | Pilot-Ancillary HPWH | Summer DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHWinter DR Event Hours | ID | General Service | Pilot-Ancillary HPWH | Winter DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHAnnual O&M Cost | ID | General Service | Pilot-Ancillary HPWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHAnnual O&M Cost per MW | ID | General Service | Pilot-Ancillary HPWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHAnnual Program Administration Cost | ID | General Service | Pilot-Ancillary HPWH | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHCost of Equip + Install | ID | General Service | Pilot-Ancillary HPWH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHCost of Equip + Install (per kW basis) | ID | General Service | Pilot-Ancillary HPWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHDe-rate | ID | General Service | Pilot-Ancillary HPWH | De-rate | capacity equivalence factor | 0 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHNet to Gross Ratio (free ridership) | ID | General Service | Pilot-Ancillary HPWH | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHPer Customer Annual Marketing/Recruitment Cost | ID | General Service | Pilot-Ancillary HPWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as Smart Thermostats |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHPer Participant Annual Incentive | ID | General Service | Pilot-Ancillary HPWH | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHPer kW Annual Incentive | ID | General Service | Pilot-Ancillary HPWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHProgram Development Cost | ID | General Service | Pilot-Ancillary HPWH | Program Development Cost | $/program | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHProgram Life | ID | General Service | Pilot-Ancillary HPWH | Program Life | years | 0 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServicePilot-Ancillary HPWHProgram Start Year | ID | General Service | Pilot-Ancillary HPWH | Program Start Year | year | 0 | 0 |  | General ServiceProgram Start Year | Market PotentialID
IDResidentialParent-Ancillary HPWHSummer DR Event Hours | ID | Residential | Parent-Ancillary HPWH | Summer DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialParent-Ancillary HPWHWinter DR Event Hours | ID | Residential | Parent-Ancillary HPWH | Winter DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialParent-Ancillary HPWHAnnual O&M Cost | ID | Residential | Parent-Ancillary HPWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialParent-Ancillary HPWHAnnual O&M Cost per MW | ID | Residential | Parent-Ancillary HPWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialParent-Ancillary HPWHAnnual Program Administration Cost | ID | Residential | Parent-Ancillary HPWH | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialParent-Ancillary HPWHCost of Equip + Install | ID | Residential | Parent-Ancillary HPWH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialParent-Ancillary HPWHCost of Equip + Install (per kW basis) | ID | Residential | Parent-Ancillary HPWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialParent-Ancillary HPWHDe-rate | ID | Residential | Parent-Ancillary HPWH | De-rate | capacity equivalence factor | 0 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialParent-Ancillary HPWHNet to Gross Ratio (free ridership) | ID | Residential | Parent-Ancillary HPWH | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialParent-Ancillary HPWHPer Customer Annual Marketing/Recruitment Cost | ID | Residential | Parent-Ancillary HPWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as Smart Thermostats |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialParent-Ancillary HPWHPer Participant Annual Incentive | ID | Residential | Parent-Ancillary HPWH | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialParent-Ancillary HPWHPer kW Annual Incentive | ID | Residential | Parent-Ancillary HPWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialParent-Ancillary HPWHProgram Development Cost | ID | Residential | Parent-Ancillary HPWH | Program Development Cost | $/program | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialParent-Ancillary HPWHProgram Life | ID | Residential | Parent-Ancillary HPWH | Program Life | years | 0 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialParent-Ancillary HPWHProgram Start Year | ID | Residential | Parent-Ancillary HPWH | Program Start Year | year | 0 | 0 |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHSummer DR Event Hours | ID | General Service | Parent-Ancillary HPWH | Summer DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHWinter DR Event Hours | ID | General Service | Parent-Ancillary HPWH | Winter DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHAnnual O&M Cost | ID | General Service | Parent-Ancillary HPWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHAnnual O&M Cost per MW | ID | General Service | Parent-Ancillary HPWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHAnnual Program Administration Cost | ID | General Service | Parent-Ancillary HPWH | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHCost of Equip + Install | ID | General Service | Parent-Ancillary HPWH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHCost of Equip + Install (per kW basis) | ID | General Service | Parent-Ancillary HPWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHDe-rate | ID | General Service | Parent-Ancillary HPWH | De-rate | capacity equivalence factor | 0 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHNet to Gross Ratio (free ridership) | ID | General Service | Parent-Ancillary HPWH | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHPer Customer Annual Marketing/Recruitment Cost | ID | General Service | Parent-Ancillary HPWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as Smart Thermostats |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHPer Participant Annual Incentive | ID | General Service | Parent-Ancillary HPWH | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHPer kW Annual Incentive | ID | General Service | Parent-Ancillary HPWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHProgram Development Cost | ID | General Service | Parent-Ancillary HPWH | Program Development Cost | $/program | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHProgram Life | ID | General Service | Parent-Ancillary HPWH | Program Life | years | 0 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceParent-Ancillary HPWHProgram Start Year | ID | General Service | Parent-Ancillary HPWH | Program Start Year | year | 0 | 0 |  | General ServiceProgram Start Year | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHSummer DR Event Hours | ID | Residential | Pilot-CTA-2045 ERWH | Summer DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHWinter DR Event Hours | ID | Residential | Pilot-CTA-2045 ERWH | Winter DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHAnnual O&M Cost | ID | Residential | Pilot-CTA-2045 ERWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHAnnual O&M Cost per MW | ID | Residential | Pilot-CTA-2045 ERWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHAnnual Program Administration Cost | ID | Residential | Pilot-CTA-2045 ERWH | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHCost of Equip + Install | ID | Residential | Pilot-CTA-2045 ERWH | Cost of Equip + Install | $/tech | 0 | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 for these customers)- average customer will be $170 |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHCost of Equip + Install (per kW basis) | ID | Residential | Pilot-CTA-2045 ERWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHDe-rate | ID | Residential | Pilot-CTA-2045 ERWH | De-rate | capacity equivalence factor | 0 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHNet to Gross Ratio (free ridership) | ID | Residential | Pilot-CTA-2045 ERWH | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHPer Customer Annual Marketing/Recruitment Cost | ID | Residential | Pilot-CTA-2045 ERWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as Smart Thermostats |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHPer Participant Annual Incentive | ID | Residential | Pilot-CTA-2045 ERWH | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHPer kW Annual Incentive | ID | Residential | Pilot-CTA-2045 ERWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHProgram Development Cost | ID | Residential | Pilot-CTA-2045 ERWH | Program Development Cost | $/program | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHProgram Life | ID | Residential | Pilot-CTA-2045 ERWH | Program Life | years | 0 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialPilot-CTA-2045 ERWHProgram Start Year | ID | Residential | Pilot-CTA-2045 ERWH | Program Start Year | year | 0 | 0 |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHSummer DR Event Hours | ID | General Service | Pilot-CTA-2045 ERWH | Summer DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHWinter DR Event Hours | ID | General Service | Pilot-CTA-2045 ERWH | Winter DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHAnnual O&M Cost | ID | General Service | Pilot-CTA-2045 ERWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHAnnual O&M Cost per MW | ID | General Service | Pilot-CTA-2045 ERWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHAnnual Program Administration Cost | ID | General Service | Pilot-CTA-2045 ERWH | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHCost of Equip + Install | ID | General Service | Pilot-CTA-2045 ERWH | Cost of Equip + Install | $/tech | 0 | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 install cost for these customers)- average customer will be $170 |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHCost of Equip + Install (per kW basis) | ID | General Service | Pilot-CTA-2045 ERWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHDe-rate | ID | General Service | Pilot-CTA-2045 ERWH | De-rate | capacity equivalence factor | 0 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHNet to Gross Ratio (free ridership) | ID | General Service | Pilot-CTA-2045 ERWH | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHPer Customer Annual Marketing/Recruitment Cost | ID | General Service | Pilot-CTA-2045 ERWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as Smart Thermostats |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHPer Participant Annual Incentive | ID | General Service | Pilot-CTA-2045 ERWH | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHPer kW Annual Incentive | ID | General Service | Pilot-CTA-2045 ERWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHProgram Development Cost | ID | General Service | Pilot-CTA-2045 ERWH | Program Development Cost | $/program | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHProgram Life | ID | General Service | Pilot-CTA-2045 ERWH | Program Life | years | 0 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServicePilot-CTA-2045 ERWHProgram Start Year | ID | General Service | Pilot-CTA-2045 ERWH | Program Start Year | year | 0 | 0 |  | General ServiceProgram Start Year | Market PotentialID
IDResidentialParent-CTA-2045 ERWHSummer DR Event Hours | ID | Residential | Parent-CTA-2045 ERWH | Summer DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialParent-CTA-2045 ERWHWinter DR Event Hours | ID | Residential | Parent-CTA-2045 ERWH | Winter DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialParent-CTA-2045 ERWHAnnual O&M Cost | ID | Residential | Parent-CTA-2045 ERWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialParent-CTA-2045 ERWHAnnual O&M Cost per MW | ID | Residential | Parent-CTA-2045 ERWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialParent-CTA-2045 ERWHAnnual Program Administration Cost | ID | Residential | Parent-CTA-2045 ERWH | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialParent-CTA-2045 ERWHCost of Equip + Install | ID | Residential | Parent-CTA-2045 ERWH | Cost of Equip + Install | $/tech | 0 | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 for these customers)- average customer will be $170 |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialParent-CTA-2045 ERWHCost of Equip + Install (per kW basis) | ID | Residential | Parent-CTA-2045 ERWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialParent-CTA-2045 ERWHDe-rate | ID | Residential | Parent-CTA-2045 ERWH | De-rate | capacity equivalence factor | 0 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialParent-CTA-2045 ERWHNet to Gross Ratio (free ridership) | ID | Residential | Parent-CTA-2045 ERWH | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialParent-CTA-2045 ERWHPer Customer Annual Marketing/Recruitment Cost | ID | Residential | Parent-CTA-2045 ERWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as Smart Thermostats |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialParent-CTA-2045 ERWHPer Participant Annual Incentive | ID | Residential | Parent-CTA-2045 ERWH | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialParent-CTA-2045 ERWHPer kW Annual Incentive | ID | Residential | Parent-CTA-2045 ERWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialParent-CTA-2045 ERWHProgram Development Cost | ID | Residential | Parent-CTA-2045 ERWH | Program Development Cost | $/program | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialParent-CTA-2045 ERWHProgram Life | ID | Residential | Parent-CTA-2045 ERWH | Program Life | years | 0 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialParent-CTA-2045 ERWHProgram Start Year | ID | Residential | Parent-CTA-2045 ERWH | Program Start Year | year | 0 | 0 |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHSummer DR Event Hours | ID | General Service | Parent-CTA-2045 ERWH | Summer DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHWinter DR Event Hours | ID | General Service | Parent-CTA-2045 ERWH | Winter DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHAnnual O&M Cost | ID | General Service | Parent-CTA-2045 ERWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHAnnual O&M Cost per MW | ID | General Service | Parent-CTA-2045 ERWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHAnnual Program Administration Cost | ID | General Service | Parent-CTA-2045 ERWH | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHCost of Equip + Install | ID | General Service | Parent-CTA-2045 ERWH | Cost of Equip + Install | $/tech | 0 | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 install cost for these customers)- average customer will be $170 |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHCost of Equip + Install (per kW basis) | ID | General Service | Parent-CTA-2045 ERWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHDe-rate | ID | General Service | Parent-CTA-2045 ERWH | De-rate | capacity equivalence factor | 0 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHNet to Gross Ratio (free ridership) | ID | General Service | Parent-CTA-2045 ERWH | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHPer Customer Annual Marketing/Recruitment Cost | ID | General Service | Parent-CTA-2045 ERWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as Smart Thermostats |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHPer Participant Annual Incentive | ID | General Service | Parent-CTA-2045 ERWH | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHPer kW Annual Incentive | ID | General Service | Parent-CTA-2045 ERWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHProgram Development Cost | ID | General Service | Parent-CTA-2045 ERWH | Program Development Cost | $/program | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHProgram Life | ID | General Service | Parent-CTA-2045 ERWH | Program Life | years | 0 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceParent-CTA-2045 ERWHProgram Start Year | ID | General Service | Parent-CTA-2045 ERWH | Program Start Year | year | 0 | 0 |  | General ServiceProgram Start Year | Market PotentialID
IDResidentialPilot-Ancillary ERWHSummer DR Event Hours | ID | Residential | Pilot-Ancillary ERWH | Summer DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialPilot-Ancillary ERWHWinter DR Event Hours | ID | Residential | Pilot-Ancillary ERWH | Winter DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialPilot-Ancillary ERWHAnnual O&M Cost | ID | Residential | Pilot-Ancillary ERWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialPilot-Ancillary ERWHAnnual O&M Cost per MW | ID | Residential | Pilot-Ancillary ERWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialPilot-Ancillary ERWHAnnual Program Administration Cost | ID | Residential | Pilot-Ancillary ERWH | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialPilot-Ancillary ERWHCost of Equip + Install | ID | Residential | Pilot-Ancillary ERWH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialPilot-Ancillary ERWHCost of Equip + Install (per kW basis) | ID | Residential | Pilot-Ancillary ERWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialPilot-Ancillary ERWHDe-rate | ID | Residential | Pilot-Ancillary ERWH | De-rate | capacity equivalence factor | 0 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialPilot-Ancillary ERWHNet to Gross Ratio (free ridership) | ID | Residential | Pilot-Ancillary ERWH | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialPilot-Ancillary ERWHPer Customer Annual Marketing/Recruitment Cost | ID | Residential | Pilot-Ancillary ERWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as Smart Thermostats |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialPilot-Ancillary ERWHPer Participant Annual Incentive | ID | Residential | Pilot-Ancillary ERWH | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialPilot-Ancillary ERWHPer kW Annual Incentive | ID | Residential | Pilot-Ancillary ERWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialPilot-Ancillary ERWHProgram Development Cost | ID | Residential | Pilot-Ancillary ERWH | Program Development Cost | $/program | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialPilot-Ancillary ERWHProgram Life | ID | Residential | Pilot-Ancillary ERWH | Program Life | years | 0 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialPilot-Ancillary ERWHProgram Start Year | ID | Residential | Pilot-Ancillary ERWH | Program Start Year | year | 0 | 0 |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHSummer DR Event Hours | ID | General Service | Pilot-Ancillary ERWH | Summer DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHWinter DR Event Hours | ID | General Service | Pilot-Ancillary ERWH | Winter DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHAnnual O&M Cost | ID | General Service | Pilot-Ancillary ERWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHAnnual O&M Cost per MW | ID | General Service | Pilot-Ancillary ERWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHAnnual Program Administration Cost | ID | General Service | Pilot-Ancillary ERWH | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHCost of Equip + Install | ID | General Service | Pilot-Ancillary ERWH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHCost of Equip + Install (per kW basis) | ID | General Service | Pilot-Ancillary ERWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHDe-rate | ID | General Service | Pilot-Ancillary ERWH | De-rate | capacity equivalence factor | 0 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHNet to Gross Ratio (free ridership) | ID | General Service | Pilot-Ancillary ERWH | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHPer Customer Annual Marketing/Recruitment Cost | ID | General Service | Pilot-Ancillary ERWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as Smart Thermostats |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHPer Participant Annual Incentive | ID | General Service | Pilot-Ancillary ERWH | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHPer kW Annual Incentive | ID | General Service | Pilot-Ancillary ERWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHProgram Development Cost | ID | General Service | Pilot-Ancillary ERWH | Program Development Cost | $/program | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHProgram Life | ID | General Service | Pilot-Ancillary ERWH | Program Life | years | 0 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServicePilot-Ancillary ERWHProgram Start Year | ID | General Service | Pilot-Ancillary ERWH | Program Start Year | year | 0 | 0 |  | General ServiceProgram Start Year | Market PotentialID
IDResidentialParent-Ancillary ERWHSummer DR Event Hours | ID | Residential | Parent-Ancillary ERWH | Summer DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialParent-Ancillary ERWHWinter DR Event Hours | ID | Residential | Parent-Ancillary ERWH | Winter DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialParent-Ancillary ERWHAnnual O&M Cost | ID | Residential | Parent-Ancillary ERWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialParent-Ancillary ERWHAnnual O&M Cost per MW | ID | Residential | Parent-Ancillary ERWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialParent-Ancillary ERWHAnnual Program Administration Cost | ID | Residential | Parent-Ancillary ERWH | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialParent-Ancillary ERWHCost of Equip + Install | ID | Residential | Parent-Ancillary ERWH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialParent-Ancillary ERWHCost of Equip + Install (per kW basis) | ID | Residential | Parent-Ancillary ERWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialParent-Ancillary ERWHDe-rate | ID | Residential | Parent-Ancillary ERWH | De-rate | capacity equivalence factor | 0 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialParent-Ancillary ERWHNet to Gross Ratio (free ridership) | ID | Residential | Parent-Ancillary ERWH | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialParent-Ancillary ERWHPer Customer Annual Marketing/Recruitment Cost | ID | Residential | Parent-Ancillary ERWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as Smart Thermostats |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialParent-Ancillary ERWHPer Participant Annual Incentive | ID | Residential | Parent-Ancillary ERWH | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialParent-Ancillary ERWHPer kW Annual Incentive | ID | Residential | Parent-Ancillary ERWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialParent-Ancillary ERWHProgram Development Cost | ID | Residential | Parent-Ancillary ERWH | Program Development Cost | $/program | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialParent-Ancillary ERWHProgram Life | ID | Residential | Parent-Ancillary ERWH | Program Life | years | 0 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialParent-Ancillary ERWHProgram Start Year | ID | Residential | Parent-Ancillary ERWH | Program Start Year | year | 0 | 0 |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHSummer DR Event Hours | ID | General Service | Parent-Ancillary ERWH | Summer DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHWinter DR Event Hours | ID | General Service | Parent-Ancillary ERWH | Winter DR Event Hours | hours/year | 0 | 25 total events around 3 hrs ea. |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHAnnual O&M Cost | ID | General Service | Parent-Ancillary ERWH | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHAnnual O&M Cost per MW | ID | General Service | Parent-Ancillary ERWH | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHAnnual Program Administration Cost | ID | General Service | Parent-Ancillary ERWH | Annual Program Administration Cost | $/yr | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHCost of Equip + Install | ID | General Service | Parent-Ancillary ERWH | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHCost of Equip + Install (per kW basis) | ID | General Service | Parent-Ancillary ERWH | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHDe-rate | ID | General Service | Parent-Ancillary ERWH | De-rate | capacity equivalence factor | 0 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHNet to Gross Ratio (free ridership) | ID | General Service | Parent-Ancillary ERWH | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHPer Customer Annual Marketing/Recruitment Cost | ID | General Service | Parent-Ancillary ERWH | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | Same as Smart Thermostats |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHPer Participant Annual Incentive | ID | General Service | Parent-Ancillary ERWH | Per Participant Annual Incentive | $/participant/year | 0 | Assume $2/month year round |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHPer kW Annual Incentive | ID | General Service | Parent-Ancillary ERWH | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHProgram Development Cost | ID | General Service | Parent-Ancillary ERWH | Program Development Cost | $/program | 0 | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHProgram Life | ID | General Service | Parent-Ancillary ERWH | Program Life | years | 0 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceParent-Ancillary ERWHProgram Start Year | ID | General Service | Parent-Ancillary ERWH | Program Start Year | year | 0 | 0 |  | General ServiceProgram Start Year | Market PotentialID
IDResidentialDLC Smart AppliancesSummer DR Event Hours | ID | Residential | DLC Smart Appliances | Summer DR Event Hours | hours/year | 528 | Pacificorp: Six hours on-peak period each summer weekday |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialDLC Smart AppliancesWinter DR Event Hours | ID | Residential | DLC Smart Appliances | Winter DR Event Hours | hours/year | 528 | Pacificorp: Six hours on-peak period each winter weekday |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialDLC Smart AppliancesAnnual O&M Cost | ID | Residential | DLC Smart Appliances | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialDLC Smart AppliancesAnnual O&M Cost per MW | ID | Residential | DLC Smart Appliances | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialDLC Smart AppliancesAnnual Program Administration Cost | ID | Residential | DLC Smart Appliances | Annual Program Administration Cost | $/yr | 28505.1219 | Share of Cost as noted in table at right |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialDLC Smart AppliancesCost of Equip + Install | ID | Residential | DLC Smart Appliances | Cost of Equip + Install | $/tech | 300 | Google research revealed devices range anywhere between $150 -400. Need wifi hub or some sort to connect devices. See email between Dave & Victoria 5-9-16 |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialDLC Smart AppliancesCost of Equip + Install (per kW basis) | ID | Residential | DLC Smart Appliances | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialDLC Smart AppliancesDe-rate | ID | Residential | DLC Smart Appliances | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialDLC Smart AppliancesNet to Gross Ratio (free ridership) | ID | Residential | DLC Smart Appliances | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialDLC Smart AppliancesPer Customer Annual Marketing/Recruitment Cost | ID | Residential | DLC Smart Appliances | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | 0 |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialDLC Smart AppliancesPer Participant Annual Incentive | ID | Residential | DLC Smart Appliances | Per Participant Annual Incentive | $/participant/year | 0 | 0 |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialDLC Smart AppliancesPer kW Annual Incentive | ID | Residential | DLC Smart Appliances | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialDLC Smart AppliancesProgram Development Cost | ID | Residential | DLC Smart Appliances | Program Development Cost | $/program | 23754.2683 | Share of Cost as noted in table at right |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialDLC Smart AppliancesProgram Life | ID | Residential | DLC Smart Appliances | Program Life | years | 8 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialDLC Smart AppliancesProgram Start Year | ID | Residential | DLC Smart Appliances | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesSummer DR Event Hours | ID | General Service | DLC Smart Appliances | Summer DR Event Hours | hours/year | 528 | Pacificorp: Six hours on-peak period each summer weekday |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesWinter DR Event Hours | ID | General Service | DLC Smart Appliances | Winter DR Event Hours | hours/year | 528 | Pacificorp: Six hours on-peak period each winter weekday |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesAnnual O&M Cost | ID | General Service | DLC Smart Appliances | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesAnnual O&M Cost per MW | ID | General Service | DLC Smart Appliances | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesAnnual Program Administration Cost | ID | General Service | DLC Smart Appliances | Annual Program Administration Cost | $/yr | 3938.9155 | Share of Cost as noted in table at right |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesCost of Equip + Install | ID | General Service | DLC Smart Appliances | Cost of Equip + Install | $/tech | 300 | Google research revealed devices range anywhere between $150 -400. Need wifi hub or some sort to connect devices. See email between Dave & Victoria 5-9-16 |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesCost of Equip + Install (per kW basis) | ID | General Service | DLC Smart Appliances | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesDe-rate | ID | General Service | DLC Smart Appliances | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesNet to Gross Ratio (free ridership) | ID | General Service | DLC Smart Appliances | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesPer Customer Annual Marketing/Recruitment Cost | ID | General Service | DLC Smart Appliances | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | 0 |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesPer Participant Annual Incentive | ID | General Service | DLC Smart Appliances | Per Participant Annual Incentive | $/participant/year | 0 | 0 |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesPer kW Annual Incentive | ID | General Service | DLC Smart Appliances | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesProgram Development Cost | ID | General Service | DLC Smart Appliances | Program Development Cost | $/program | 3282.4296 | Share of Cost as noted in table at right |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesProgram Life | ID | General Service | DLC Smart Appliances | Program Life | years | 8 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceDLC Smart AppliancesProgram Start Year | ID | General Service | DLC Smart Appliances | Program Start Year | year | 2026 | 0 |  | General ServiceProgram Start Year | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingSummer DR Event Hours | ID | Res-EV | DLC Electric Vehicle Charging | Summer DR Event Hours | hours/year | 0 | Pacificorp: Six hours on-peak period each summer weekday |  | Res-EVSummer DR Event Hours | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingWinter DR Event Hours | ID | Res-EV | DLC Electric Vehicle Charging | Winter DR Event Hours | hours/year | 0 | Pacificorp: Six hours on-peak period each winter weekday |  | Res-EVWinter DR Event Hours | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingAnnual O&M Cost | ID | Res-EV | DLC Electric Vehicle Charging | Annual O&M Cost | $/participant/year | 0 | 2024 Avista Update: $45 per car (300 cars minimum) |  | Res-EVAnnual O&M Cost | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingAnnual O&M Cost per MW | ID | Res-EV | DLC Electric Vehicle Charging | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | Res-EVAnnual O&M Cost per MW | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingAnnual Program Administration Cost | ID | Res-EV | DLC Electric Vehicle Charging | Annual Program Administration Cost | $/yr | 0 | 2024 Avista Update: Share of Cost as noted in table at right |  | Res-EVAnnual Program Administration Cost | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingCost of Equip + Install | ID | Res-EV | DLC Electric Vehicle Charging | Cost of Equip + Install | $/tech | 0 | 10/26: $1766 from Avista 2019 EVSE report. Instead of covering cost fo equipment, Avista wants to model offering a partial incentive. Benchmarked $500 based on WA rebates. OLD: Updated cost of equipment and install to $700 per Avista email on 8/25/2020 |  | Res-EVCost of Equip + Install | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingCost of Equip + Install (per kW basis) | ID | Res-EV | DLC Electric Vehicle Charging | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | Res-EVCost of Equip + Install (per kW basis) | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingDe-rate | ID | Res-EV | DLC Electric Vehicle Charging | De-rate | capacity equivalence factor | 0 | 0 |  | Res-EVDe-rate | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingNet to Gross Ratio (free ridership) | ID | Res-EV | DLC Electric Vehicle Charging | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | Res-EVNet to Gross Ratio (free ridership) | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingPer Customer Annual Marketing/Recruitment Cost | ID | Res-EV | DLC Electric Vehicle Charging | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | 2024 Avista Update |  | Res-EVPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingPer Participant Annual Incentive | ID | Res-EV | DLC Electric Vehicle Charging | Per Participant Annual Incentive | $/participant/year | 0 | 2024 Avista Update: $5/month for 1st year; $0 if cust charges 3+ times on peak |  | Res-EVPer Participant Annual Incentive | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingPer kW Annual Incentive | ID | Res-EV | DLC Electric Vehicle Charging | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | Res-EVPer kW Annual Incentive | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingProgram Development Cost | ID | Res-EV | DLC Electric Vehicle Charging | Program Development Cost | $/program | 0 | Share of Cost as noted in table at right |  | Res-EVProgram Development Cost | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingProgram Life | ID | Res-EV | DLC Electric Vehicle Charging | Program Life | years | 0 | 0 |  | Res-EVProgram Life | Market PotentialID
IDRes-EVDLC Electric Vehicle ChargingProgram Start Year | ID | Res-EV | DLC Electric Vehicle Charging | Program Start Year | year | 0 | 2024 Avista Update |  | Res-EVProgram Start Year | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingSummer DR Event Hours | ID | GS-EV | DLC Electric Vehicle Charging | Summer DR Event Hours | hours/year |  |  |  | GS-EVSummer DR Event Hours | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingWinter DR Event Hours | ID | GS-EV | DLC Electric Vehicle Charging | Winter DR Event Hours | hours/year |  |  |  | GS-EVWinter DR Event Hours | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingAnnual O&M Cost | ID | GS-EV | DLC Electric Vehicle Charging | Annual O&M Cost | $/participant/year |  |  |  | GS-EVAnnual O&M Cost | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingAnnual O&M Cost per MW | ID | GS-EV | DLC Electric Vehicle Charging | Annual O&M Cost per MW | $/MW @meter |  |  |  | GS-EVAnnual O&M Cost per MW | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingAnnual Program Administration Cost | ID | GS-EV | DLC Electric Vehicle Charging | Annual Program Administration Cost | $/yr |  |  |  | GS-EVAnnual Program Administration Cost | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingCost of Equip + Install | ID | GS-EV | DLC Electric Vehicle Charging | Cost of Equip + Install | $/tech |  |  |  | GS-EVCost of Equip + Install | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingCost of Equip + Install (per kW basis) | ID | GS-EV | DLC Electric Vehicle Charging | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | GS-EVCost of Equip + Install (per kW basis) | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingDe-rate | ID | GS-EV | DLC Electric Vehicle Charging | De-rate | capacity equivalence factor |  |  |  | GS-EVDe-rate | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingNet to Gross Ratio (free ridership) | ID | GS-EV | DLC Electric Vehicle Charging | Net to Gross Ratio (free ridership) | ratio |  |  |  | GS-EVNet to Gross Ratio (free ridership) | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingPer Customer Annual Marketing/Recruitment Cost | ID | GS-EV | DLC Electric Vehicle Charging | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | GS-EVPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingPer Participant Annual Incentive | ID | GS-EV | DLC Electric Vehicle Charging | Per Participant Annual Incentive | $/participant/year |  |  |  | GS-EVPer Participant Annual Incentive | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingPer kW Annual Incentive | ID | GS-EV | DLC Electric Vehicle Charging | Per kW Annual Incentive | $/kW @meter/year |  |  |  | GS-EVPer kW Annual Incentive | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingProgram Development Cost | ID | GS-EV | DLC Electric Vehicle Charging | Program Development Cost | $/program |  |  |  | GS-EVProgram Development Cost | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingProgram Life | ID | GS-EV | DLC Electric Vehicle Charging | Program Life | years |  |  |  | GS-EVProgram Life | Market PotentialID
IDGS-EVDLC Electric Vehicle ChargingProgram Start Year | ID | GS-EV | DLC Electric Vehicle Charging | Program Start Year | year |  |  |  | GS-EVProgram Start Year | Market PotentialID
IDRes-EVAncillary EVSummer DR Event Hours | ID | Res-EV | Ancillary EV | Summer DR Event Hours | hours/year | 528 | Pacificorp: Six hours on-peak period each summer weekday |  | Res-EVSummer DR Event Hours | Market PotentialID
IDRes-EVAncillary EVWinter DR Event Hours | ID | Res-EV | Ancillary EV | Winter DR Event Hours | hours/year | 528 | Pacificorp: Six hours on-peak period each winter weekday |  | Res-EVWinter DR Event Hours | Market PotentialID
IDRes-EVAncillary EVAnnual O&M Cost | ID | Res-EV | Ancillary EV | Annual O&M Cost | $/participant/year | 0 | Zero for Ancillary |  | Res-EVAnnual O&M Cost | Market PotentialID
IDRes-EVAncillary EVAnnual O&M Cost per MW | ID | Res-EV | Ancillary EV | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | Res-EVAnnual O&M Cost per MW | Market PotentialID
IDRes-EVAncillary EVAnnual Program Administration Cost | ID | Res-EV | Ancillary EV | Annual Program Administration Cost | $/yr | 13213.1014 | Share of Cost as noted in table at right |  | Res-EVAnnual Program Administration Cost | Market PotentialID
IDRes-EVAncillary EVCost of Equip + Install | ID | Res-EV | Ancillary EV | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | Res-EVCost of Equip + Install | Market PotentialID
IDRes-EVAncillary EVCost of Equip + Install (per kW basis) | ID | Res-EV | Ancillary EV | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | Res-EVCost of Equip + Install (per kW basis) | Market PotentialID
IDRes-EVAncillary EVDe-rate | ID | Res-EV | Ancillary EV | De-rate | capacity equivalence factor | 1 | 0 |  | Res-EVDe-rate | Market PotentialID
IDRes-EVAncillary EVNet to Gross Ratio (free ridership) | ID | Res-EV | Ancillary EV | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | Res-EVNet to Gross Ratio (free ridership) | Market PotentialID
IDRes-EVAncillary EVPer Customer Annual Marketing/Recruitment Cost | ID | Res-EV | Ancillary EV | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | Assumption $50 for RAP C&I, MAP = RAPx1.2 |  | Res-EVPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDRes-EVAncillary EVPer Participant Annual Incentive | ID | Res-EV | Ancillary EV | Per Participant Annual Incentive | $/participant/year | 0 | Avista would provide a rate based charger or give a rebate on it, with no further incentives |  | Res-EVPer Participant Annual Incentive | Market PotentialID
IDRes-EVAncillary EVPer kW Annual Incentive | ID | Res-EV | Ancillary EV | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | Res-EVPer kW Annual Incentive | Market PotentialID
IDRes-EVAncillary EVProgram Development Cost | ID | Res-EV | Ancillary EV | Program Development Cost | $/program | 16516.3768 | Share of Cost as noted in table at right |  | Res-EVProgram Development Cost | Market PotentialID
IDRes-EVAncillary EVProgram Life | ID | Res-EV | Ancillary EV | Program Life | years | 8 | 0 |  | Res-EVProgram Life | Market PotentialID
IDRes-EVAncillary EVProgram Start Year | ID | Res-EV | Ancillary EV | Program Start Year | year | 2025 | 2024 Avista Update |  | Res-EVProgram Start Year | Market PotentialID
IDGS-EVAncillary EVSummer DR Event Hours | ID | GS-EV | Ancillary EV | Summer DR Event Hours | hours/year | 528 | Pacificorp: Six hours on-peak period each summer weekday |  | GS-EVSummer DR Event Hours | Market PotentialID
IDGS-EVAncillary EVWinter DR Event Hours | ID | GS-EV | Ancillary EV | Winter DR Event Hours | hours/year | 528 | Pacificorp: Six hours on-peak period each winter weekday |  | GS-EVWinter DR Event Hours | Market PotentialID
IDGS-EVAncillary EVAnnual O&M Cost | ID | GS-EV | Ancillary EV | Annual O&M Cost | $/participant/year | 0 | Zero for Ancillary |  | GS-EVAnnual O&M Cost | Market PotentialID
IDGS-EVAncillary EVAnnual O&M Cost per MW | ID | GS-EV | Ancillary EV | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | GS-EVAnnual O&M Cost per MW | Market PotentialID
IDGS-EVAncillary EVAnnual Program Administration Cost | ID | GS-EV | Ancillary EV | Annual Program Administration Cost | $/yr | 8799.0432 | Share of Cost as noted in table at right |  | GS-EVAnnual Program Administration Cost | Market PotentialID
IDGS-EVAncillary EVCost of Equip + Install | ID | GS-EV | Ancillary EV | Cost of Equip + Install | $/tech | 0 | Zero for Ancillary |  | GS-EVCost of Equip + Install | Market PotentialID
IDGS-EVAncillary EVCost of Equip + Install (per kW basis) | ID | GS-EV | Ancillary EV | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | GS-EVCost of Equip + Install (per kW basis) | Market PotentialID
IDGS-EVAncillary EVDe-rate | ID | GS-EV | Ancillary EV | De-rate | capacity equivalence factor | 1 | 0 |  | GS-EVDe-rate | Market PotentialID
IDGS-EVAncillary EVNet to Gross Ratio (free ridership) | ID | GS-EV | Ancillary EV | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | GS-EVNet to Gross Ratio (free ridership) | Market PotentialID
IDGS-EVAncillary EVPer Customer Annual Marketing/Recruitment Cost | ID | GS-EV | Ancillary EV | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 62.5 | 25% higher than residential |  | GS-EVPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGS-EVAncillary EVPer Participant Annual Incentive | ID | GS-EV | Ancillary EV | Per Participant Annual Incentive | $/participant/year | 0 | Avista would provide a rate based charger or give a rebate on it, with no further incentives |  | GS-EVPer Participant Annual Incentive | Market PotentialID
IDGS-EVAncillary EVPer kW Annual Incentive | ID | GS-EV | Ancillary EV | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | GS-EVPer kW Annual Incentive | Market PotentialID
IDGS-EVAncillary EVProgram Development Cost | ID | GS-EV | Ancillary EV | Program Development Cost | $/program | 10998.8039 | Share of Cost as noted in table at right |  | GS-EVProgram Development Cost | Market PotentialID
IDGS-EVAncillary EVProgram Life | ID | GS-EV | Ancillary EV | Program Life | years | 8 | 0 |  | GS-EVProgram Life | Market PotentialID
IDGS-EVAncillary EVProgram Start Year | ID | GS-EV | Ancillary EV | Program Start Year | year | 2025 | 2024 Avista Update |  | GS-EVProgram Start Year | Market PotentialID
IDGeneral ServiceThird Party ContractsSummer DR Event Hours | ID | General Service | Third Party Contracts | Summer DR Event Hours | hours/year |  |  |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceThird Party ContractsWinter DR Event Hours | ID | General Service | Third Party Contracts | Winter DR Event Hours | hours/year |  |  |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceThird Party ContractsAnnual O&M Cost | ID | General Service | Third Party Contracts | Annual O&M Cost | $/participant/year |  |  |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceThird Party ContractsAnnual O&M Cost per MW | ID | General Service | Third Party Contracts | Annual O&M Cost per MW | $/MW @meter |  |  |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceThird Party ContractsAnnual Program Administration Cost | ID | General Service | Third Party Contracts | Annual Program Administration Cost | $/yr |  |  |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceThird Party ContractsCost of Equip + Install | ID | General Service | Third Party Contracts | Cost of Equip + Install | $/tech |  |  |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceThird Party ContractsCost of Equip + Install (per kW basis) | ID | General Service | Third Party Contracts | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceThird Party ContractsDe-rate | ID | General Service | Third Party Contracts | De-rate | capacity equivalence factor |  |  |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceThird Party ContractsNet to Gross Ratio (free ridership) | ID | General Service | Third Party Contracts | Net to Gross Ratio (free ridership) | ratio |  |  |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceThird Party ContractsPer Customer Annual Marketing/Recruitment Cost | ID | General Service | Third Party Contracts | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceThird Party ContractsPer Participant Annual Incentive | ID | General Service | Third Party Contracts | Per Participant Annual Incentive | $/participant/year |  |  |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceThird Party ContractsPer kW Annual Incentive | ID | General Service | Third Party Contracts | Per kW Annual Incentive | $/kW @meter/year |  |  |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceThird Party ContractsProgram Development Cost | ID | General Service | Third Party Contracts | Program Development Cost | $/program |  |  |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceThird Party ContractsProgram Life | ID | General Service | Third Party Contracts | Program Life | years |  |  |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceThird Party ContractsProgram Start Year | ID | General Service | Third Party Contracts | Program Start Year | year |  |  |  | General ServiceProgram Start Year | Market PotentialID
IDLarge General ServiceThird Party ContractsSummer DR Event Hours | ID | Large General Service | Third Party Contracts | Summer DR Event Hours | hours/year | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  | Large General ServiceSummer DR Event Hours | Market PotentialID
IDLarge General ServiceThird Party ContractsWinter DR Event Hours | ID | Large General Service | Third Party Contracts | Winter DR Event Hours | hours/year | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  | Large General ServiceWinter DR Event Hours | Market PotentialID
IDLarge General ServiceThird Party ContractsAnnual O&M Cost | ID | Large General Service | Third Party Contracts | Annual O&M Cost | $/participant/year | 0 | included in 3rd Party Program Admin Cost |  | Large General ServiceAnnual O&M Cost | Market PotentialID
IDLarge General ServiceThird Party ContractsAnnual O&M Cost per MW | ID | Large General Service | Third Party Contracts | Annual O&M Cost per MW | $/MW @meter | 80000 | included in 3rd Party Program Admin Cost |  | Large General ServiceAnnual O&M Cost per MW | Market PotentialID
IDLarge General ServiceThird Party ContractsAnnual Program Administration Cost | ID | Large General Service | Third Party Contracts | Annual Program Administration Cost | $/yr | 0 | 0 |  | Large General ServiceAnnual Program Administration Cost | Market PotentialID
IDLarge General ServiceThird Party ContractsCost of Equip + Install | ID | Large General Service | Third Party Contracts | Cost of Equip + Install | $/tech | 0 | included in 3rd Party Program Admin Cost |  | Large General ServiceCost of Equip + Install | Market PotentialID
IDLarge General ServiceThird Party ContractsCost of Equip + Install (per kW basis) | ID | Large General Service | Third Party Contracts | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | included in 3rd Party Program Admin Cost |  | Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDLarge General ServiceThird Party ContractsDe-rate | ID | Large General Service | Third Party Contracts | De-rate | capacity equivalence factor | 1 | 0 |  | Large General ServiceDe-rate | Market PotentialID
IDLarge General ServiceThird Party ContractsNet to Gross Ratio (free ridership) | ID | Large General Service | Third Party Contracts | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDLarge General ServiceThird Party ContractsPer Customer Annual Marketing/Recruitment Cost | ID | Large General Service | Third Party Contracts | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | included in 3rd Party Program Admin Cost |  | Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDLarge General ServiceThird Party ContractsPer Participant Annual Incentive | ID | Large General Service | Third Party Contracts | Per Participant Annual Incentive | $/participant/year | 0 | 0 |  | Large General ServicePer Participant Annual Incentive | Market PotentialID
IDLarge General ServiceThird Party ContractsPer kW Annual Incentive | ID | Large General Service | Third Party Contracts | Per kW Annual Incentive | $/kW @meter/year | 0 | included in 3rd Party Program Admin Cost. Capacity reserve incentive pmt given to customers typically in range of $10 to $70 per kW-year |  | Large General ServicePer kW Annual Incentive | Market PotentialID
IDLarge General ServiceThird Party ContractsProgram Development Cost | ID | Large General Service | Third Party Contracts | Program Development Cost | $/program | 0 | No startup costs; Would be included in 3rd Party Costs |  | Large General ServiceProgram Development Cost | Market PotentialID
IDLarge General ServiceThird Party ContractsProgram Life | ID | Large General Service | Third Party Contracts | Program Life | years | 3 | 0 |  | Large General ServiceProgram Life | Market PotentialID
IDLarge General ServiceThird Party ContractsProgram Start Year | ID | Large General Service | Third Party Contracts | Program Start Year | year | 2028 | 0 |  | Large General ServiceProgram Start Year | Market PotentialID
IDExtra Large General ServiceThird Party ContractsSummer DR Event Hours | ID | Extra Large General Service | Third Party Contracts | Summer DR Event Hours | hours/year | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  | Extra Large General ServiceSummer DR Event Hours | Market PotentialID
IDExtra Large General ServiceThird Party ContractsWinter DR Event Hours | ID | Extra Large General Service | Third Party Contracts | Winter DR Event Hours | hours/year | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  | Extra Large General ServiceWinter DR Event Hours | Market PotentialID
IDExtra Large General ServiceThird Party ContractsAnnual O&M Cost | ID | Extra Large General Service | Third Party Contracts | Annual O&M Cost | $/participant/year | 0 | included in 3rd Party Program Admin Cost |  | Extra Large General ServiceAnnual O&M Cost | Market PotentialID
IDExtra Large General ServiceThird Party ContractsAnnual O&M Cost per MW | ID | Extra Large General Service | Third Party Contracts | Annual O&M Cost per MW | $/MW @meter | 80000 | included in 3rd Party Program Admin Cost |  | Extra Large General ServiceAnnual O&M Cost per MW | Market PotentialID
IDExtra Large General ServiceThird Party ContractsAnnual Program Administration Cost | ID | Extra Large General Service | Third Party Contracts | Annual Program Administration Cost | $/yr | 0 | 0 |  | Extra Large General ServiceAnnual Program Administration Cost | Market PotentialID
IDExtra Large General ServiceThird Party ContractsCost of Equip + Install | ID | Extra Large General Service | Third Party Contracts | Cost of Equip + Install | $/tech | 0 | included in 3rd Party Program Admin Cost |  | Extra Large General ServiceCost of Equip + Install | Market PotentialID
IDExtra Large General ServiceThird Party ContractsCost of Equip + Install (per kW basis) | ID | Extra Large General Service | Third Party Contracts | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | included in 3rd Party Program Admin Cost |  | Extra Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDExtra Large General ServiceThird Party ContractsDe-rate | ID | Extra Large General Service | Third Party Contracts | De-rate | capacity equivalence factor | 1 | 0 |  | Extra Large General ServiceDe-rate | Market PotentialID
IDExtra Large General ServiceThird Party ContractsNet to Gross Ratio (free ridership) | ID | Extra Large General Service | Third Party Contracts | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | Extra Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDExtra Large General ServiceThird Party ContractsPer Customer Annual Marketing/Recruitment Cost | ID | Extra Large General Service | Third Party Contracts | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | included in 3rd Party Program Admin Cost |  | Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDExtra Large General ServiceThird Party ContractsPer Participant Annual Incentive | ID | Extra Large General Service | Third Party Contracts | Per Participant Annual Incentive | $/participant/year | 0 | 0 |  | Extra Large General ServicePer Participant Annual Incentive | Market PotentialID
IDExtra Large General ServiceThird Party ContractsPer kW Annual Incentive | ID | Extra Large General Service | Third Party Contracts | Per kW Annual Incentive | $/kW @meter/year | 0 | included in 3rd Party Program Admin Cost. Capacity reserve incentive pmt given to customers typically in range of $10 to $70 per kW-year |  | Extra Large General ServicePer kW Annual Incentive | Market PotentialID
IDExtra Large General ServiceThird Party ContractsProgram Development Cost | ID | Extra Large General Service | Third Party Contracts | Program Development Cost | $/program | 0 | No startup costs; Would be included in 3rd Party Costs |  | Extra Large General ServiceProgram Development Cost | Market PotentialID
IDExtra Large General ServiceThird Party ContractsProgram Life | ID | Extra Large General Service | Third Party Contracts | Program Life | years | 3 | 0 |  | Extra Large General ServiceProgram Life | Market PotentialID
IDExtra Large General ServiceThird Party ContractsProgram Start Year | ID | Extra Large General Service | Third Party Contracts | Program Start Year | year | 2028 | 0 |  | Extra Large General ServiceProgram Start Year | Market PotentialID
IDGeneral ServiceAncillary Third PartySummer DR Event Hours | ID | General Service | Ancillary Third Party | Summer DR Event Hours | hours/year |  |  |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceAncillary Third PartyWinter DR Event Hours | ID | General Service | Ancillary Third Party | Winter DR Event Hours | hours/year |  |  |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceAncillary Third PartyAnnual O&M Cost | ID | General Service | Ancillary Third Party | Annual O&M Cost | $/participant/year |  |  |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceAncillary Third PartyAnnual O&M Cost per MW | ID | General Service | Ancillary Third Party | Annual O&M Cost per MW | $/MW @meter |  |  |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceAncillary Third PartyAnnual Program Administration Cost | ID | General Service | Ancillary Third Party | Annual Program Administration Cost | $/yr |  |  |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceAncillary Third PartyCost of Equip + Install | ID | General Service | Ancillary Third Party | Cost of Equip + Install | $/tech |  |  |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceAncillary Third PartyCost of Equip + Install (per kW basis) | ID | General Service | Ancillary Third Party | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceAncillary Third PartyDe-rate | ID | General Service | Ancillary Third Party | De-rate | capacity equivalence factor |  |  |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceAncillary Third PartyNet to Gross Ratio (free ridership) | ID | General Service | Ancillary Third Party | Net to Gross Ratio (free ridership) | ratio |  |  |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceAncillary Third PartyPer Customer Annual Marketing/Recruitment Cost | ID | General Service | Ancillary Third Party | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceAncillary Third PartyPer Participant Annual Incentive | ID | General Service | Ancillary Third Party | Per Participant Annual Incentive | $/participant/year |  |  |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceAncillary Third PartyPer kW Annual Incentive | ID | General Service | Ancillary Third Party | Per kW Annual Incentive | $/kW @meter/year |  |  |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceAncillary Third PartyProgram Development Cost | ID | General Service | Ancillary Third Party | Program Development Cost | $/program |  |  |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceAncillary Third PartyProgram Life | ID | General Service | Ancillary Third Party | Program Life | years |  |  |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceAncillary Third PartyProgram Start Year | ID | General Service | Ancillary Third Party | Program Start Year | year |  |  |  | General ServiceProgram Start Year | Market PotentialID
IDLarge General ServiceAncillary Third PartySummer DR Event Hours | ID | Large General Service | Ancillary Third Party | Summer DR Event Hours | hours/year | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  | Large General ServiceSummer DR Event Hours | Market PotentialID
IDLarge General ServiceAncillary Third PartyWinter DR Event Hours | ID | Large General Service | Ancillary Third Party | Winter DR Event Hours | hours/year | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  | Large General ServiceWinter DR Event Hours | Market PotentialID
IDLarge General ServiceAncillary Third PartyAnnual O&M Cost | ID | Large General Service | Ancillary Third Party | Annual O&M Cost | $/participant/year | 0 | included in 3rd Party Program Admin Cost |  | Large General ServiceAnnual O&M Cost | Market PotentialID
IDLarge General ServiceAncillary Third PartyAnnual O&M Cost per MW | ID | Large General Service | Ancillary Third Party | Annual O&M Cost per MW | $/MW @meter | 40000 | Half for Ancillary |  | Large General ServiceAnnual O&M Cost per MW | Market PotentialID
IDLarge General ServiceAncillary Third PartyAnnual Program Administration Cost | ID | Large General Service | Ancillary Third Party | Annual Program Administration Cost | $/yr | 0 | 0 |  | Large General ServiceAnnual Program Administration Cost | Market PotentialID
IDLarge General ServiceAncillary Third PartyCost of Equip + Install | ID | Large General Service | Ancillary Third Party | Cost of Equip + Install | $/tech | 0 | included in 3rd Party Program Admin Cost |  | Large General ServiceCost of Equip + Install | Market PotentialID
IDLarge General ServiceAncillary Third PartyCost of Equip + Install (per kW basis) | ID | Large General Service | Ancillary Third Party | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | included in 3rd Party Program Admin Cost |  | Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDLarge General ServiceAncillary Third PartyDe-rate | ID | Large General Service | Ancillary Third Party | De-rate | capacity equivalence factor | 1 | 0 |  | Large General ServiceDe-rate | Market PotentialID
IDLarge General ServiceAncillary Third PartyNet to Gross Ratio (free ridership) | ID | Large General Service | Ancillary Third Party | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDLarge General ServiceAncillary Third PartyPer Customer Annual Marketing/Recruitment Cost | ID | Large General Service | Ancillary Third Party | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | included in 3rd Party Program Admin Cost |  | Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDLarge General ServiceAncillary Third PartyPer Participant Annual Incentive | ID | Large General Service | Ancillary Third Party | Per Participant Annual Incentive | $/participant/year | 0 | 0 |  | Large General ServicePer Participant Annual Incentive | Market PotentialID
IDLarge General ServiceAncillary Third PartyPer kW Annual Incentive | ID | Large General Service | Ancillary Third Party | Per kW Annual Incentive | $/kW @meter/year | 0 | included in 3rd Party Program Admin Cost. Capacity reserve incentive pmt given to customers typically in range of $10 to $70 per kW-year |  | Large General ServicePer kW Annual Incentive | Market PotentialID
IDLarge General ServiceAncillary Third PartyProgram Development Cost | ID | Large General Service | Ancillary Third Party | Program Development Cost | $/program | 0 | No startup costs; Would be included in 3rd Party Costs |  | Large General ServiceProgram Development Cost | Market PotentialID
IDLarge General ServiceAncillary Third PartyProgram Life | ID | Large General Service | Ancillary Third Party | Program Life | years | 3 | 0 |  | Large General ServiceProgram Life | Market PotentialID
IDLarge General ServiceAncillary Third PartyProgram Start Year | ID | Large General Service | Ancillary Third Party | Program Start Year | year | 2028 | 0 |  | Large General ServiceProgram Start Year | Market PotentialID
IDExtra Large General ServiceAncillary Third PartySummer DR Event Hours | ID | Extra Large General Service | Ancillary Third Party | Summer DR Event Hours | hours/year | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  | Extra Large General ServiceSummer DR Event Hours | Market PotentialID
IDExtra Large General ServiceAncillary Third PartyWinter DR Event Hours | ID | Extra Large General Service | Ancillary Third Party | Winter DR Event Hours | hours/year | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  | Extra Large General ServiceWinter DR Event Hours | Market PotentialID
IDExtra Large General ServiceAncillary Third PartyAnnual O&M Cost | ID | Extra Large General Service | Ancillary Third Party | Annual O&M Cost | $/participant/year | 0 | included in 3rd Party Program Admin Cost |  | Extra Large General ServiceAnnual O&M Cost | Market PotentialID
IDExtra Large General ServiceAncillary Third PartyAnnual O&M Cost per MW | ID | Extra Large General Service | Ancillary Third Party | Annual O&M Cost per MW | $/MW @meter | 40000 | Half for Ancillary |  | Extra Large General ServiceAnnual O&M Cost per MW | Market PotentialID
IDExtra Large General ServiceAncillary Third PartyAnnual Program Administration Cost | ID | Extra Large General Service | Ancillary Third Party | Annual Program Administration Cost | $/yr | 0 | 0 |  | Extra Large General ServiceAnnual Program Administration Cost | Market PotentialID
IDExtra Large General ServiceAncillary Third PartyCost of Equip + Install | ID | Extra Large General Service | Ancillary Third Party | Cost of Equip + Install | $/tech | 0 | included in 3rd Party Program Admin Cost |  | Extra Large General ServiceCost of Equip + Install | Market PotentialID
IDExtra Large General ServiceAncillary Third PartyCost of Equip + Install (per kW basis) | ID | Extra Large General Service | Ancillary Third Party | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | included in 3rd Party Program Admin Cost |  | Extra Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDExtra Large General ServiceAncillary Third PartyDe-rate | ID | Extra Large General Service | Ancillary Third Party | De-rate | capacity equivalence factor | 1 | 0 |  | Extra Large General ServiceDe-rate | Market PotentialID
IDExtra Large General ServiceAncillary Third PartyNet to Gross Ratio (free ridership) | ID | Extra Large General Service | Ancillary Third Party | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | Extra Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDExtra Large General ServiceAncillary Third PartyPer Customer Annual Marketing/Recruitment Cost | ID | Extra Large General Service | Ancillary Third Party | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | included in 3rd Party Program Admin Cost |  | Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDExtra Large General ServiceAncillary Third PartyPer Participant Annual Incentive | ID | Extra Large General Service | Ancillary Third Party | Per Participant Annual Incentive | $/participant/year | 0 | 0 |  | Extra Large General ServicePer Participant Annual Incentive | Market PotentialID
IDExtra Large General ServiceAncillary Third PartyPer kW Annual Incentive | ID | Extra Large General Service | Ancillary Third Party | Per kW Annual Incentive | $/kW @meter/year | 0 | included in 3rd Party Program Admin Cost. Capacity reserve incentive pmt given to customers typically in range of $10 to $70 per kW-year |  | Extra Large General ServicePer kW Annual Incentive | Market PotentialID
IDExtra Large General ServiceAncillary Third PartyProgram Development Cost | ID | Extra Large General Service | Ancillary Third Party | Program Development Cost | $/program | 0 | No startup costs; Would be included in 3rd Party Costs |  | Extra Large General ServiceProgram Development Cost | Market PotentialID
IDExtra Large General ServiceAncillary Third PartyProgram Life | ID | Extra Large General Service | Ancillary Third Party | Program Life | years | 3 | 0 |  | Extra Large General ServiceProgram Life | Market PotentialID
IDExtra Large General ServiceAncillary Third PartyProgram Start Year | ID | Extra Large General Service | Ancillary Third Party | Program Start Year | year | 2028 | 0 |  | Extra Large General ServiceProgram Start Year | Market PotentialID
IDGeneral ServiceThermal Energy StorageSummer DR Event Hours | ID | General Service | Thermal Energy Storage | Summer DR Event Hours | hours/year | 36 | Same as TOU, six hours on peak period each summer |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceThermal Energy StorageWinter DR Event Hours | ID | General Service | Thermal Energy Storage | Winter DR Event Hours | hours/year | 0 | 0 |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceThermal Energy StorageAnnual O&M Cost | ID | General Service | Thermal Energy Storage | Annual O&M Cost | $/participant/year | 84 | Assumption of 5% equipment costs |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceThermal Energy StorageAnnual O&M Cost per MW | ID | General Service | Thermal Energy Storage | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceThermal Energy StorageAnnual Program Administration Cost | ID | General Service | Thermal Energy Storage | Annual Program Administration Cost | $/yr | 14412.4371 | Share of Cost as noted in table at right |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceThermal Energy StorageCost of Equip + Install | ID | General Service | Thermal Energy Storage | Cost of Equip + Install | $/tech | 0 | 0 |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceThermal Energy StorageCost of Equip + Install (per kW basis) | ID | General Service | Thermal Energy Storage | Cost of Equip + Install (per kW basis) | $/kW @meter | 1680 | Utility Dive Article, Ice Energy Implementer cost |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceThermal Energy StorageDe-rate | ID | General Service | Thermal Energy Storage | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceThermal Energy StorageNet to Gross Ratio (free ridership) | ID | General Service | Thermal Energy Storage | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceThermal Energy StoragePer Customer Annual Marketing/Recruitment Cost | ID | General Service | Thermal Energy Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 100 | Assumption $100 for RAP C&I, MAP = RAPx1.2 |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceThermal Energy StoragePer Participant Annual Incentive | ID | General Service | Thermal Energy Storage | Per Participant Annual Incentive | $/participant/year | 0 | No incentive. Program purchases & installs unit. |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceThermal Energy StoragePer kW Annual Incentive | ID | General Service | Thermal Energy Storage | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceThermal Energy StorageProgram Development Cost | ID | General Service | Thermal Energy Storage | Program Development Cost | $/program | 18015.5463 | Share of Cost as noted in table at right |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceThermal Energy StorageProgram Life | ID | General Service | Thermal Energy Storage | Program Life | years | 20 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceThermal Energy StorageProgram Start Year | ID | General Service | Thermal Energy Storage | Program Start Year | year | 2026 | 0 |  | General ServiceProgram Start Year | Market PotentialID
IDLarge General ServiceThermal Energy StorageSummer DR Event Hours | ID | Large General Service | Thermal Energy Storage | Summer DR Event Hours | hours/year | 36 | Same as TOU, six hours on peak period each summer |  | Large General ServiceSummer DR Event Hours | Market PotentialID
IDLarge General ServiceThermal Energy StorageWinter DR Event Hours | ID | Large General Service | Thermal Energy Storage | Winter DR Event Hours | hours/year | 0 | 0 |  | Large General ServiceWinter DR Event Hours | Market PotentialID
IDLarge General ServiceThermal Energy StorageAnnual O&M Cost | ID | Large General Service | Thermal Energy Storage | Annual O&M Cost | $/participant/year | 420 | Assumption of 5% equipment costs |  | Large General ServiceAnnual O&M Cost | Market PotentialID
IDLarge General ServiceThermal Energy StorageAnnual O&M Cost per MW | ID | Large General Service | Thermal Energy Storage | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | Large General ServiceAnnual O&M Cost per MW | Market PotentialID
IDLarge General ServiceThermal Energy StorageAnnual Program Administration Cost | ID | Large General Service | Thermal Energy Storage | Annual Program Administration Cost | $/yr | 8339.0989 | Share of Cost as noted in table at right |  | Large General ServiceAnnual Program Administration Cost | Market PotentialID
IDLarge General ServiceThermal Energy StorageCost of Equip + Install | ID | Large General Service | Thermal Energy Storage | Cost of Equip + Install | $/tech | 0 | 0 |  | Large General ServiceCost of Equip + Install | Market PotentialID
IDLarge General ServiceThermal Energy StorageCost of Equip + Install (per kW basis) | ID | Large General Service | Thermal Energy Storage | Cost of Equip + Install (per kW basis) | $/kW @meter | 8400 | Utility Dive Article, Ice Energy Implementer cost |  | Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDLarge General ServiceThermal Energy StorageDe-rate | ID | Large General Service | Thermal Energy Storage | De-rate | capacity equivalence factor | 1 | 0 |  | Large General ServiceDe-rate | Market PotentialID
IDLarge General ServiceThermal Energy StorageNet to Gross Ratio (free ridership) | ID | Large General Service | Thermal Energy Storage | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDLarge General ServiceThermal Energy StoragePer Customer Annual Marketing/Recruitment Cost | ID | Large General Service | Thermal Energy Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 100 | Assumption $100 for RAP C&I, MAP = RAPx1.2 |  | Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDLarge General ServiceThermal Energy StoragePer Participant Annual Incentive | ID | Large General Service | Thermal Energy Storage | Per Participant Annual Incentive | $/participant/year | 0 | No incentive. Program purchases & installs unit. |  | Large General ServicePer Participant Annual Incentive | Market PotentialID
IDLarge General ServiceThermal Energy StoragePer kW Annual Incentive | ID | Large General Service | Thermal Energy Storage | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | Large General ServicePer kW Annual Incentive | Market PotentialID
IDLarge General ServiceThermal Energy StorageProgram Development Cost | ID | Large General Service | Thermal Energy Storage | Program Development Cost | $/program | 10423.8736 | Share of Cost as noted in table at right |  | Large General ServiceProgram Development Cost | Market PotentialID
IDLarge General ServiceThermal Energy StorageProgram Life | ID | Large General Service | Thermal Energy Storage | Program Life | years | 20 | 0 |  | Large General ServiceProgram Life | Market PotentialID
IDLarge General ServiceThermal Energy StorageProgram Start Year | ID | Large General Service | Thermal Energy Storage | Program Start Year | year | 2026 | 0 |  | Large General ServiceProgram Start Year | Market PotentialID
IDExtra Large General ServiceThermal Energy StorageSummer DR Event Hours | ID | Extra Large General Service | Thermal Energy Storage | Summer DR Event Hours | hours/year | 36 | Same as TOU, six hours on peak period each summer |  | Extra Large General ServiceSummer DR Event Hours | Market PotentialID
IDExtra Large General ServiceThermal Energy StorageWinter DR Event Hours | ID | Extra Large General Service | Thermal Energy Storage | Winter DR Event Hours | hours/year | 0 | 0 |  | Extra Large General ServiceWinter DR Event Hours | Market PotentialID
IDExtra Large General ServiceThermal Energy StorageAnnual O&M Cost | ID | Extra Large General Service | Thermal Energy Storage | Annual O&M Cost | $/participant/year | 420 | Assumption of 5% equipment costs |  | Extra Large General ServiceAnnual O&M Cost | Market PotentialID
IDExtra Large General ServiceThermal Energy StorageAnnual O&M Cost per MW | ID | Extra Large General Service | Thermal Energy Storage | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | Extra Large General ServiceAnnual O&M Cost per MW | Market PotentialID
IDExtra Large General ServiceThermal Energy StorageAnnual Program Administration Cost | ID | Extra Large General Service | Thermal Energy Storage | Annual Program Administration Cost | $/yr | 111.9793 | Share of Cost as noted in table at right |  | Extra Large General ServiceAnnual Program Administration Cost | Market PotentialID
IDExtra Large General ServiceThermal Energy StorageCost of Equip + Install | ID | Extra Large General Service | Thermal Energy Storage | Cost of Equip + Install | $/tech | 0 | 0 |  | Extra Large General ServiceCost of Equip + Install | Market PotentialID
IDExtra Large General ServiceThermal Energy StorageCost of Equip + Install (per kW basis) | ID | Extra Large General Service | Thermal Energy Storage | Cost of Equip + Install (per kW basis) | $/kW @meter | 8400 | Utility Dive Article, Ice Energy Implementer cost |  | Extra Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDExtra Large General ServiceThermal Energy StorageDe-rate | ID | Extra Large General Service | Thermal Energy Storage | De-rate | capacity equivalence factor | 1 | 0 |  | Extra Large General ServiceDe-rate | Market PotentialID
IDExtra Large General ServiceThermal Energy StorageNet to Gross Ratio (free ridership) | ID | Extra Large General Service | Thermal Energy Storage | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | Extra Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDExtra Large General ServiceThermal Energy StoragePer Customer Annual Marketing/Recruitment Cost | ID | Extra Large General Service | Thermal Energy Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 100 | Assumption $100 for RAP C&I, MAP = RAPx1.2 |  | Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDExtra Large General ServiceThermal Energy StoragePer Participant Annual Incentive | ID | Extra Large General Service | Thermal Energy Storage | Per Participant Annual Incentive | $/participant/year | 0 | No incentive. Program purchases & installs unit. |  | Extra Large General ServicePer Participant Annual Incentive | Market PotentialID
IDExtra Large General ServiceThermal Energy StoragePer kW Annual Incentive | ID | Extra Large General Service | Thermal Energy Storage | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | Extra Large General ServicePer kW Annual Incentive | Market PotentialID
IDExtra Large General ServiceThermal Energy StorageProgram Development Cost | ID | Extra Large General Service | Thermal Energy Storage | Program Development Cost | $/program | 139.9741 | Share of Cost as noted in table at right |  | Extra Large General ServiceProgram Development Cost | Market PotentialID
IDExtra Large General ServiceThermal Energy StorageProgram Life | ID | Extra Large General Service | Thermal Energy Storage | Program Life | years | 20 | 0 |  | Extra Large General ServiceProgram Life | Market PotentialID
IDExtra Large General ServiceThermal Energy StorageProgram Start Year | ID | Extra Large General Service | Thermal Energy Storage | Program Start Year | year | 2026 | 0 |  | Extra Large General ServiceProgram Start Year | Market PotentialID
IDResidentialBattery Energy StorageSummer DR Event Hours | ID | Residential | Battery Energy Storage | Summer DR Event Hours | hours/year | 120 | Xcel Energy CO Renewable Battery Connect: up to 60 events per year, assuming 4-hr events. |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialBattery Energy StorageWinter DR Event Hours | ID | Residential | Battery Energy Storage | Winter DR Event Hours | hours/year | 120 | Xcel Energy CO Renewable Battery Connect: up to 60 events per year, assuming 4-hr events. |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialBattery Energy StorageAnnual O&M Cost | ID | Residential | Battery Energy Storage | Annual O&M Cost | $/participant/year | 50 | 2023 PAC CPA: PNNL 2019 ($10/kW per year) |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialBattery Energy StorageAnnual O&M Cost per MW | ID | Residential | Battery Energy Storage | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialBattery Energy StorageAnnual Program Administration Cost | ID | Residential | Battery Energy Storage | Annual Program Administration Cost | $/yr | 18273.2226 | half FTE @ $150,000 |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialBattery Energy StorageCost of Equip + Install | ID | Residential | Battery Energy Storage | Cost of Equip + Install | $/tech | 2500 | Xcel Energy CO Renewable Battery Connect: $500/enrolled kW for enrolling in the program (capped at 50% of battery equipment costs) |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialBattery Energy StorageCost of Equip + Install (per kW basis) | ID | Residential | Battery Energy Storage | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialBattery Energy StorageDe-rate | ID | Residential | Battery Energy Storage | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialBattery Energy StorageNet to Gross Ratio (free ridership) | ID | Residential | Battery Energy Storage | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialBattery Energy StoragePer Customer Annual Marketing/Recruitment Cost | ID | Residential | Battery Energy Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | 0 |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialBattery Energy StoragePer Participant Annual Incentive | ID | Residential | Battery Energy Storage | Per Participant Annual Incentive | $/participant/year | 0 | 0 |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialBattery Energy StoragePer kW Annual Incentive | ID | Residential | Battery Energy Storage | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialBattery Energy StorageProgram Development Cost | ID | Residential | Battery Energy Storage | Program Development Cost | $/program | 22841.5283 | 0 |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialBattery Energy StorageProgram Life | ID | Residential | Battery Energy Storage | Program Life | years | 15 | NREL |  | ResidentialProgram Life | Market PotentialID
IDResidentialBattery Energy StorageProgram Start Year | ID | Residential | Battery Energy Storage | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServiceBattery Energy StorageSummer DR Event Hours | ID | General Service | Battery Energy Storage | Summer DR Event Hours | hours/year | 120 | Xcel Energy CO Renewable Battery Connect: up to 60 events per year, assuming 4-hr events. |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceBattery Energy StorageWinter DR Event Hours | ID | General Service | Battery Energy Storage | Winter DR Event Hours | hours/year | 120 | Xcel Energy CO Renewable Battery Connect: up to 60 events per year, assuming 4-hr events. |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceBattery Energy StorageAnnual O&M Cost | ID | General Service | Battery Energy Storage | Annual O&M Cost | $/participant/year | 50 | 2023 PAC CPA: PNNL 2019 ($10/kW per year) |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceBattery Energy StorageAnnual O&M Cost per MW | ID | General Service | Battery Energy Storage | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceBattery Energy StorageAnnual Program Administration Cost | ID | General Service | Battery Energy Storage | Annual Program Administration Cost | $/yr | 3240 | half FTE @ $150,000 |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceBattery Energy StorageCost of Equip + Install | ID | General Service | Battery Energy Storage | Cost of Equip + Install | $/tech | 2500 | Xcel Energy CO Renewable Battery Connect: $500/enrolled kW for enrolling in the program (capped at 50% of battery equipment costs) |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceBattery Energy StorageCost of Equip + Install (per kW basis) | ID | General Service | Battery Energy Storage | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceBattery Energy StorageDe-rate | ID | General Service | Battery Energy Storage | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceBattery Energy StorageNet to Gross Ratio (free ridership) | ID | General Service | Battery Energy Storage | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceBattery Energy StoragePer Customer Annual Marketing/Recruitment Cost | ID | General Service | Battery Energy Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | 0 |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceBattery Energy StoragePer Participant Annual Incentive | ID | General Service | Battery Energy Storage | Per Participant Annual Incentive | $/participant/year | 0 | 0 |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceBattery Energy StoragePer kW Annual Incentive | ID | General Service | Battery Energy Storage | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceBattery Energy StorageProgram Development Cost | ID | General Service | Battery Energy Storage | Program Development Cost | $/program | 4050 | 0 |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceBattery Energy StorageProgram Life | ID | General Service | Battery Energy Storage | Program Life | years | 15 | NREL |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceBattery Energy StorageProgram Start Year | ID | General Service | Battery Energy Storage | Program Start Year | year | 2026 | Assumed rollout could piggyback on Utility's TOU |  | General ServiceProgram Start Year | Market PotentialID
IDLarge General ServiceBattery Energy StorageSummer DR Event Hours | ID | Large General Service | Battery Energy Storage | Summer DR Event Hours | hours/year |  |  |  | Large General ServiceSummer DR Event Hours | Market PotentialID
IDLarge General ServiceBattery Energy StorageWinter DR Event Hours | ID | Large General Service | Battery Energy Storage | Winter DR Event Hours | hours/year |  |  |  | Large General ServiceWinter DR Event Hours | Market PotentialID
IDLarge General ServiceBattery Energy StorageAnnual O&M Cost | ID | Large General Service | Battery Energy Storage | Annual O&M Cost | $/participant/year |  |  |  | Large General ServiceAnnual O&M Cost | Market PotentialID
IDLarge General ServiceBattery Energy StorageAnnual O&M Cost per MW | ID | Large General Service | Battery Energy Storage | Annual O&M Cost per MW | $/MW @meter |  |  |  | Large General ServiceAnnual O&M Cost per MW | Market PotentialID
IDLarge General ServiceBattery Energy StorageAnnual Program Administration Cost | ID | Large General Service | Battery Energy Storage | Annual Program Administration Cost | $/yr |  |  |  | Large General ServiceAnnual Program Administration Cost | Market PotentialID
IDLarge General ServiceBattery Energy StorageCost of Equip + Install | ID | Large General Service | Battery Energy Storage | Cost of Equip + Install | $/tech |  |  |  | Large General ServiceCost of Equip + Install | Market PotentialID
IDLarge General ServiceBattery Energy StorageCost of Equip + Install (per kW basis) | ID | Large General Service | Battery Energy Storage | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDLarge General ServiceBattery Energy StorageDe-rate | ID | Large General Service | Battery Energy Storage | De-rate | capacity equivalence factor |  |  |  | Large General ServiceDe-rate | Market PotentialID
IDLarge General ServiceBattery Energy StorageNet to Gross Ratio (free ridership) | ID | Large General Service | Battery Energy Storage | Net to Gross Ratio (free ridership) | ratio |  |  |  | Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDLarge General ServiceBattery Energy StoragePer Customer Annual Marketing/Recruitment Cost | ID | Large General Service | Battery Energy Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDLarge General ServiceBattery Energy StoragePer Participant Annual Incentive | ID | Large General Service | Battery Energy Storage | Per Participant Annual Incentive | $/participant/year |  |  |  | Large General ServicePer Participant Annual Incentive | Market PotentialID
IDLarge General ServiceBattery Energy StoragePer kW Annual Incentive | ID | Large General Service | Battery Energy Storage | Per kW Annual Incentive | $/kW @meter/year |  |  |  | Large General ServicePer kW Annual Incentive | Market PotentialID
IDLarge General ServiceBattery Energy StorageProgram Development Cost | ID | Large General Service | Battery Energy Storage | Program Development Cost | $/program |  |  |  | Large General ServiceProgram Development Cost | Market PotentialID
IDLarge General ServiceBattery Energy StorageProgram Life | ID | Large General Service | Battery Energy Storage | Program Life | years |  |  |  | Large General ServiceProgram Life | Market PotentialID
IDLarge General ServiceBattery Energy StorageProgram Start Year | ID | Large General Service | Battery Energy Storage | Program Start Year | year |  |  |  | Large General ServiceProgram Start Year | Market PotentialID
IDExtra Large General ServiceBattery Energy StorageSummer DR Event Hours | ID | Extra Large General Service | Battery Energy Storage | Summer DR Event Hours | hours/year |  |  |  | Extra Large General ServiceSummer DR Event Hours | Market PotentialID
IDExtra Large General ServiceBattery Energy StorageWinter DR Event Hours | ID | Extra Large General Service | Battery Energy Storage | Winter DR Event Hours | hours/year |  |  |  | Extra Large General ServiceWinter DR Event Hours | Market PotentialID
IDExtra Large General ServiceBattery Energy StorageAnnual O&M Cost | ID | Extra Large General Service | Battery Energy Storage | Annual O&M Cost | $/participant/year |  |  |  | Extra Large General ServiceAnnual O&M Cost | Market PotentialID
IDExtra Large General ServiceBattery Energy StorageAnnual O&M Cost per MW | ID | Extra Large General Service | Battery Energy Storage | Annual O&M Cost per MW | $/MW @meter |  |  |  | Extra Large General ServiceAnnual O&M Cost per MW | Market PotentialID
IDExtra Large General ServiceBattery Energy StorageAnnual Program Administration Cost | ID | Extra Large General Service | Battery Energy Storage | Annual Program Administration Cost | $/yr |  |  |  | Extra Large General ServiceAnnual Program Administration Cost | Market PotentialID
IDExtra Large General ServiceBattery Energy StorageCost of Equip + Install | ID | Extra Large General Service | Battery Energy Storage | Cost of Equip + Install | $/tech |  |  |  | Extra Large General ServiceCost of Equip + Install | Market PotentialID
IDExtra Large General ServiceBattery Energy StorageCost of Equip + Install (per kW basis) | ID | Extra Large General Service | Battery Energy Storage | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | Extra Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDExtra Large General ServiceBattery Energy StorageDe-rate | ID | Extra Large General Service | Battery Energy Storage | De-rate | capacity equivalence factor |  |  |  | Extra Large General ServiceDe-rate | Market PotentialID
IDExtra Large General ServiceBattery Energy StorageNet to Gross Ratio (free ridership) | ID | Extra Large General Service | Battery Energy Storage | Net to Gross Ratio (free ridership) | ratio |  |  |  | Extra Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDExtra Large General ServiceBattery Energy StoragePer Customer Annual Marketing/Recruitment Cost | ID | Extra Large General Service | Battery Energy Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDExtra Large General ServiceBattery Energy StoragePer Participant Annual Incentive | ID | Extra Large General Service | Battery Energy Storage | Per Participant Annual Incentive | $/participant/year |  |  |  | Extra Large General ServicePer Participant Annual Incentive | Market PotentialID
IDExtra Large General ServiceBattery Energy StoragePer kW Annual Incentive | ID | Extra Large General Service | Battery Energy Storage | Per kW Annual Incentive | $/kW @meter/year |  |  |  | Extra Large General ServicePer kW Annual Incentive | Market PotentialID
IDExtra Large General ServiceBattery Energy StorageProgram Development Cost | ID | Extra Large General Service | Battery Energy Storage | Program Development Cost | $/program |  |  |  | Extra Large General ServiceProgram Development Cost | Market PotentialID
IDExtra Large General ServiceBattery Energy StorageProgram Life | ID | Extra Large General Service | Battery Energy Storage | Program Life | years |  |  |  | Extra Large General ServiceProgram Life | Market PotentialID
IDExtra Large General ServiceBattery Energy StorageProgram Start Year | ID | Extra Large General Service | Battery Energy Storage | Program Start Year | year |  |  |  | Extra Large General ServiceProgram Start Year | Market PotentialID
IDResidentialAncillary Battery StorageSummer DR Event Hours | ID | Residential | Ancillary Battery Storage | Summer DR Event Hours | hours/year | 36 | 0 |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialAncillary Battery StorageWinter DR Event Hours | ID | Residential | Ancillary Battery Storage | Winter DR Event Hours | hours/year | 36 | Round trip efficiency assumption: |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialAncillary Battery StorageAnnual O&M Cost | ID | Residential | Ancillary Battery Storage | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialAncillary Battery StorageAnnual O&M Cost per MW | ID | Residential | Ancillary Battery Storage | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialAncillary Battery StorageAnnual Program Administration Cost | ID | Residential | Ancillary Battery Storage | Annual Program Administration Cost | $/yr | 18273.2226 | half FTE @ $150,000 |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialAncillary Battery StorageCost of Equip + Install | ID | Residential | Ancillary Battery Storage | Cost of Equip + Install | $/tech | 0 | Customer already has device if on program |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialAncillary Battery StorageCost of Equip + Install (per kW basis) | ID | Residential | Ancillary Battery Storage | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialAncillary Battery StorageDe-rate | ID | Residential | Ancillary Battery Storage | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialAncillary Battery StorageNet to Gross Ratio (free ridership) | ID | Residential | Ancillary Battery Storage | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialAncillary Battery StoragePer Customer Annual Marketing/Recruitment Cost | ID | Residential | Ancillary Battery Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | 0 |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialAncillary Battery StoragePer Participant Annual Incentive | ID | Residential | Ancillary Battery Storage | Per Participant Annual Incentive | $/participant/year | 20 | $20 incentives to participate in ancillary |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialAncillary Battery StoragePer kW Annual Incentive | ID | Residential | Ancillary Battery Storage | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialAncillary Battery StorageProgram Development Cost | ID | Residential | Ancillary Battery Storage | Program Development Cost | $/program | 22841.5283 | 0 |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialAncillary Battery StorageProgram Life | ID | Residential | Ancillary Battery Storage | Program Life | years | 15 | NREL |  | ResidentialProgram Life | Market PotentialID
IDResidentialAncillary Battery StorageProgram Start Year | ID | Residential | Ancillary Battery Storage | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServiceAncillary Battery StorageSummer DR Event Hours | ID | General Service | Ancillary Battery Storage | Summer DR Event Hours | hours/year | 36 | 0 |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceAncillary Battery StorageWinter DR Event Hours | ID | General Service | Ancillary Battery Storage | Winter DR Event Hours | hours/year | 36 | Round trip efficiency assumption: |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceAncillary Battery StorageAnnual O&M Cost | ID | General Service | Ancillary Battery Storage | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceAncillary Battery StorageAnnual O&M Cost per MW | ID | General Service | Ancillary Battery Storage | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceAncillary Battery StorageAnnual Program Administration Cost | ID | General Service | Ancillary Battery Storage | Annual Program Administration Cost | $/yr | 3240 | half FTE @ $150,000 |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceAncillary Battery StorageCost of Equip + Install | ID | General Service | Ancillary Battery Storage | Cost of Equip + Install | $/tech | 0 | Customer already has device if on program |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceAncillary Battery StorageCost of Equip + Install (per kW basis) | ID | General Service | Ancillary Battery Storage | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceAncillary Battery StorageDe-rate | ID | General Service | Ancillary Battery Storage | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceAncillary Battery StorageNet to Gross Ratio (free ridership) | ID | General Service | Ancillary Battery Storage | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceAncillary Battery StoragePer Customer Annual Marketing/Recruitment Cost | ID | General Service | Ancillary Battery Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | 0 |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceAncillary Battery StoragePer Participant Annual Incentive | ID | General Service | Ancillary Battery Storage | Per Participant Annual Incentive | $/participant/year | 20 | $20 incentives to participate in ancillary |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceAncillary Battery StoragePer kW Annual Incentive | ID | General Service | Ancillary Battery Storage | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceAncillary Battery StorageProgram Development Cost | ID | General Service | Ancillary Battery Storage | Program Development Cost | $/program | 4050 | 0 |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceAncillary Battery StorageProgram Life | ID | General Service | Ancillary Battery Storage | Program Life | years | 15 | NREL |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceAncillary Battery StorageProgram Start Year | ID | General Service | Ancillary Battery Storage | Program Start Year | year | 2026 | Assumed rollout could piggyback on Utility's TOU |  | General ServiceProgram Start Year | Market PotentialID
IDLarge General ServiceAncillary Battery StorageSummer DR Event Hours | ID | Large General Service | Ancillary Battery Storage | Summer DR Event Hours | hours/year |  |  |  | Large General ServiceSummer DR Event Hours | Market PotentialID
IDLarge General ServiceAncillary Battery StorageWinter DR Event Hours | ID | Large General Service | Ancillary Battery Storage | Winter DR Event Hours | hours/year |  |  |  | Large General ServiceWinter DR Event Hours | Market PotentialID
IDLarge General ServiceAncillary Battery StorageAnnual O&M Cost | ID | Large General Service | Ancillary Battery Storage | Annual O&M Cost | $/participant/year |  |  |  | Large General ServiceAnnual O&M Cost | Market PotentialID
IDLarge General ServiceAncillary Battery StorageAnnual O&M Cost per MW | ID | Large General Service | Ancillary Battery Storage | Annual O&M Cost per MW | $/MW @meter |  |  |  | Large General ServiceAnnual O&M Cost per MW | Market PotentialID
IDLarge General ServiceAncillary Battery StorageAnnual Program Administration Cost | ID | Large General Service | Ancillary Battery Storage | Annual Program Administration Cost | $/yr |  |  |  | Large General ServiceAnnual Program Administration Cost | Market PotentialID
IDLarge General ServiceAncillary Battery StorageCost of Equip + Install | ID | Large General Service | Ancillary Battery Storage | Cost of Equip + Install | $/tech |  |  |  | Large General ServiceCost of Equip + Install | Market PotentialID
IDLarge General ServiceAncillary Battery StorageCost of Equip + Install (per kW basis) | ID | Large General Service | Ancillary Battery Storage | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDLarge General ServiceAncillary Battery StorageDe-rate | ID | Large General Service | Ancillary Battery Storage | De-rate | capacity equivalence factor |  |  |  | Large General ServiceDe-rate | Market PotentialID
IDLarge General ServiceAncillary Battery StorageNet to Gross Ratio (free ridership) | ID | Large General Service | Ancillary Battery Storage | Net to Gross Ratio (free ridership) | ratio |  |  |  | Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDLarge General ServiceAncillary Battery StoragePer Customer Annual Marketing/Recruitment Cost | ID | Large General Service | Ancillary Battery Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDLarge General ServiceAncillary Battery StoragePer Participant Annual Incentive | ID | Large General Service | Ancillary Battery Storage | Per Participant Annual Incentive | $/participant/year |  |  |  | Large General ServicePer Participant Annual Incentive | Market PotentialID
IDLarge General ServiceAncillary Battery StoragePer kW Annual Incentive | ID | Large General Service | Ancillary Battery Storage | Per kW Annual Incentive | $/kW @meter/year |  |  |  | Large General ServicePer kW Annual Incentive | Market PotentialID
IDLarge General ServiceAncillary Battery StorageProgram Development Cost | ID | Large General Service | Ancillary Battery Storage | Program Development Cost | $/program |  |  |  | Large General ServiceProgram Development Cost | Market PotentialID
IDLarge General ServiceAncillary Battery StorageProgram Life | ID | Large General Service | Ancillary Battery Storage | Program Life | years |  |  |  | Large General ServiceProgram Life | Market PotentialID
IDLarge General ServiceAncillary Battery StorageProgram Start Year | ID | Large General Service | Ancillary Battery Storage | Program Start Year | year |  |  |  | Large General ServiceProgram Start Year | Market PotentialID
IDExtra Large General ServiceAncillary Battery StorageSummer DR Event Hours | ID | Extra Large General Service | Ancillary Battery Storage | Summer DR Event Hours | hours/year |  |  |  | Extra Large General ServiceSummer DR Event Hours | Market PotentialID
IDExtra Large General ServiceAncillary Battery StorageWinter DR Event Hours | ID | Extra Large General Service | Ancillary Battery Storage | Winter DR Event Hours | hours/year |  |  |  | Extra Large General ServiceWinter DR Event Hours | Market PotentialID
IDExtra Large General ServiceAncillary Battery StorageAnnual O&M Cost | ID | Extra Large General Service | Ancillary Battery Storage | Annual O&M Cost | $/participant/year |  |  |  | Extra Large General ServiceAnnual O&M Cost | Market PotentialID
IDExtra Large General ServiceAncillary Battery StorageAnnual O&M Cost per MW | ID | Extra Large General Service | Ancillary Battery Storage | Annual O&M Cost per MW | $/MW @meter |  |  |  | Extra Large General ServiceAnnual O&M Cost per MW | Market PotentialID
IDExtra Large General ServiceAncillary Battery StorageAnnual Program Administration Cost | ID | Extra Large General Service | Ancillary Battery Storage | Annual Program Administration Cost | $/yr |  |  |  | Extra Large General ServiceAnnual Program Administration Cost | Market PotentialID
IDExtra Large General ServiceAncillary Battery StorageCost of Equip + Install | ID | Extra Large General Service | Ancillary Battery Storage | Cost of Equip + Install | $/tech |  |  |  | Extra Large General ServiceCost of Equip + Install | Market PotentialID
IDExtra Large General ServiceAncillary Battery StorageCost of Equip + Install (per kW basis) | ID | Extra Large General Service | Ancillary Battery Storage | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | Extra Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDExtra Large General ServiceAncillary Battery StorageDe-rate | ID | Extra Large General Service | Ancillary Battery Storage | De-rate | capacity equivalence factor |  |  |  | Extra Large General ServiceDe-rate | Market PotentialID
IDExtra Large General ServiceAncillary Battery StorageNet to Gross Ratio (free ridership) | ID | Extra Large General Service | Ancillary Battery Storage | Net to Gross Ratio (free ridership) | ratio |  |  |  | Extra Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDExtra Large General ServiceAncillary Battery StoragePer Customer Annual Marketing/Recruitment Cost | ID | Extra Large General Service | Ancillary Battery Storage | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDExtra Large General ServiceAncillary Battery StoragePer Participant Annual Incentive | ID | Extra Large General Service | Ancillary Battery Storage | Per Participant Annual Incentive | $/participant/year |  |  |  | Extra Large General ServicePer Participant Annual Incentive | Market PotentialID
IDExtra Large General ServiceAncillary Battery StoragePer kW Annual Incentive | ID | Extra Large General Service | Ancillary Battery Storage | Per kW Annual Incentive | $/kW @meter/year |  |  |  | Extra Large General ServicePer kW Annual Incentive | Market PotentialID
IDExtra Large General ServiceAncillary Battery StorageProgram Development Cost | ID | Extra Large General Service | Ancillary Battery Storage | Program Development Cost | $/program |  |  |  | Extra Large General ServiceProgram Development Cost | Market PotentialID
IDExtra Large General ServiceAncillary Battery StorageProgram Life | ID | Extra Large General Service | Ancillary Battery Storage | Program Life | years |  |  |  | Extra Large General ServiceProgram Life | Market PotentialID
IDExtra Large General ServiceAncillary Battery StorageProgram Start Year | ID | Extra Large General Service | Ancillary Battery Storage | Program Start Year | year |  |  |  | Extra Large General ServiceProgram Start Year | Market PotentialID
IDResidentialBehavioralSummer DR Event Hours | ID | Residential | Behavioral | Summer DR Event Hours | hours/year | 40 | 8 hour event window x 5 events, Consumers Energy 7am-8pm 8 hr window |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialBehavioralWinter DR Event Hours | ID | Residential | Behavioral | Winter DR Event Hours | hours/year | 40 | 8 hour event window x 5 events, Consumers Energy 7am-8pm 8 hr window |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialBehavioralAnnual O&M Cost | ID | Residential | Behavioral | Annual O&M Cost | $/participant/year | 3.25 | Oracle interview on 8/30, estimation of admin cost per household - KM heard 3 - 3.5 all inclusive- Implementation Cost |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialBehavioralAnnual O&M Cost per MW | ID | Residential | Behavioral | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialBehavioralAnnual Program Administration Cost | ID | Residential | Behavioral | Annual Program Administration Cost | $/yr | 19900.5768 | 0 |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialBehavioralCost of Equip + Install | ID | Residential | Behavioral | Cost of Equip + Install | $/tech | 0 | 0 |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialBehavioralCost of Equip + Install (per kW basis) | ID | Residential | Behavioral | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialBehavioralDe-rate | ID | Residential | Behavioral | De-rate | capacity equivalence factor | 1 | Impact Reduced to reflect diminished savings program pulls in participants who are not "high" users |  | ResidentialDe-rate | Market PotentialID
IDResidentialBehavioralNet to Gross Ratio (free ridership) | ID | Residential | Behavioral | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialBehavioralPer Customer Annual Marketing/Recruitment Cost | ID | Residential | Behavioral | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | 0 |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialBehavioralPer Participant Annual Incentive | ID | Residential | Behavioral | Per Participant Annual Incentive | $/participant/year | 0 | No Incentive for Behavioral DR - Brattle PGE Potential Study 2016 - |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialBehavioralPer kW Annual Incentive | ID | Residential | Behavioral | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialBehavioralProgram Development Cost | ID | Residential | Behavioral | Program Development Cost | $/program | 33167.628 | 0 |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialBehavioralProgram Life | ID | Residential | Behavioral | Program Life | years | 1 | MISO Res LoadMAP DSM Programs.xlsx (LRZ7) - Lifetime |  | ResidentialProgram Life | Market PotentialID
IDResidentialBehavioralProgram Start Year | ID | Residential | Behavioral | Program Start Year | year | 2026 | 0 |  | ResidentialProgram Start Year | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inSummer DR Event Hours | ID | Residential | Pilot-Time-of-Use Opt-in | Summer DR Event Hours | hours/year | 0 | Six hours on-peak period each summer weekday |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inWinter DR Event Hours | ID | Residential | Pilot-Time-of-Use Opt-in | Winter DR Event Hours | hours/year | 0 | Six hours on-peak period each winter weekday too, except for Utah |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inAnnual O&M Cost | ID | Residential | Pilot-Time-of-Use Opt-in | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inAnnual O&M Cost per MW | ID | Residential | Pilot-Time-of-Use Opt-in | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inAnnual Program Administration Cost | ID | Residential | Pilot-Time-of-Use Opt-in | Annual Program Administration Cost | $/yr | 0 | 0 |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inCost of Equip + Install | ID | Residential | Pilot-Time-of-Use Opt-in | Cost of Equip + Install | $/tech | 0 | 0 |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inCost of Equip + Install (per kW basis) | ID | Residential | Pilot-Time-of-Use Opt-in | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inDe-rate | ID | Residential | Pilot-Time-of-Use Opt-in | De-rate | capacity equivalence factor | 0 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inNet to Gross Ratio (free ridership) | ID | Residential | Pilot-Time-of-Use Opt-in | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inPer Customer Annual Marketing/Recruitment Cost | ID | Residential | Pilot-Time-of-Use Opt-in | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | 1.5x standatd $50 marketing cost because it involves more education on kW rate blocks |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inPer Participant Annual Incentive | ID | Residential | Pilot-Time-of-Use Opt-in | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inPer kW Annual Incentive | ID | Residential | Pilot-Time-of-Use Opt-in | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inProgram Development Cost | ID | Residential | Pilot-Time-of-Use Opt-in | Program Development Cost | $/program | 0 | 0 |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inProgram Life | ID | Residential | Pilot-Time-of-Use Opt-in | Program Life | years | 0 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialPilot-Time-of-Use Opt-inProgram Start Year | ID | Residential | Pilot-Time-of-Use Opt-in | Program Start Year | year | 0 | Modeling potential pilot starting in 2024 |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inSummer DR Event Hours | ID | General Service | Pilot-Time-of-Use Opt-in | Summer DR Event Hours | hours/year | 0 | Six hours on-peak period each summer weekday |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inWinter DR Event Hours | ID | General Service | Pilot-Time-of-Use Opt-in | Winter DR Event Hours | hours/year | 0 | Six hours on-peak period each winter weekday too, except for Utah |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inAnnual O&M Cost | ID | General Service | Pilot-Time-of-Use Opt-in | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inAnnual O&M Cost per MW | ID | General Service | Pilot-Time-of-Use Opt-in | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inAnnual Program Administration Cost | ID | General Service | Pilot-Time-of-Use Opt-in | Annual Program Administration Cost | $/yr | 0 | 0 |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inCost of Equip + Install | ID | General Service | Pilot-Time-of-Use Opt-in | Cost of Equip + Install | $/tech | 0 | 0 |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inCost of Equip + Install (per kW basis) | ID | General Service | Pilot-Time-of-Use Opt-in | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inDe-rate | ID | General Service | Pilot-Time-of-Use Opt-in | De-rate | capacity equivalence factor | 0 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inNet to Gross Ratio (free ridership) | ID | General Service | Pilot-Time-of-Use Opt-in | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inPer Customer Annual Marketing/Recruitment Cost | ID | General Service | Pilot-Time-of-Use Opt-in | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | 1.5x standatd $50 marketing cost because it involves more education on kW rate blocks |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inPer Participant Annual Incentive | ID | General Service | Pilot-Time-of-Use Opt-in | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inPer kW Annual Incentive | ID | General Service | Pilot-Time-of-Use Opt-in | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inProgram Development Cost | ID | General Service | Pilot-Time-of-Use Opt-in | Program Development Cost | $/program | 0 | 0 |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inProgram Life | ID | General Service | Pilot-Time-of-Use Opt-in | Program Life | years | 0 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServicePilot-Time-of-Use Opt-inProgram Start Year | ID | General Service | Pilot-Time-of-Use Opt-in | Program Start Year | year | 0 | Modeling potential pilot starting in 2024 |  | General ServiceProgram Start Year | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inSummer DR Event Hours | ID | Residential | Parent-Time-of-Use Opt-in | Summer DR Event Hours | hours/year | 528 | Six hours on-peak period each summer weekday |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inWinter DR Event Hours | ID | Residential | Parent-Time-of-Use Opt-in | Winter DR Event Hours | hours/year | 528 | Six hours on-peak period each winter weekday too, except for Utah |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inAnnual O&M Cost | ID | Residential | Parent-Time-of-Use Opt-in | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inAnnual O&M Cost per MW | ID | Residential | Parent-Time-of-Use Opt-in | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inAnnual Program Administration Cost | ID | Residential | Parent-Time-of-Use Opt-in | Annual Program Administration Cost | $/yr | 66691.6514 | 2024 Avista Update |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inCost of Equip + Install | ID | Residential | Parent-Time-of-Use Opt-in | Cost of Equip + Install | $/tech | 0 | 0 |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inCost of Equip + Install (per kW basis) | ID | Residential | Parent-Time-of-Use Opt-in | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inDe-rate | ID | Residential | Parent-Time-of-Use Opt-in | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inNet to Gross Ratio (free ridership) | ID | Residential | Parent-Time-of-Use Opt-in | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inPer Customer Annual Marketing/Recruitment Cost | ID | Residential | Parent-Time-of-Use Opt-in | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | 2024 Avista Update |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inPer Participant Annual Incentive | ID | Residential | Parent-Time-of-Use Opt-in | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inPer kW Annual Incentive | ID | Residential | Parent-Time-of-Use Opt-in | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inProgram Development Cost | ID | Residential | Parent-Time-of-Use Opt-in | Program Development Cost | $/program | 811026.4756 | 2024 Avista Update- WA dev costs are sunk($2 mil), ID costs will be half of WA @ $1mil dev costs |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inProgram Life | ID | Residential | Parent-Time-of-Use Opt-in | Program Life | years | 10 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialParent-Time-of-Use Opt-inProgram Start Year | ID | Residential | Parent-Time-of-Use Opt-in | Program Start Year | year | 2028 | WA; ID Start in 2028: 2024 Avista Update; will change ramp rate after model run |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inSummer DR Event Hours | ID | General Service | Parent-Time-of-Use Opt-in | Summer DR Event Hours | hours/year | 528 | Six hours on-peak period each summer weekday |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inWinter DR Event Hours | ID | General Service | Parent-Time-of-Use Opt-in | Winter DR Event Hours | hours/year | 528 | Six hours on-peak period each winter weekday too, except for Utah |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inAnnual O&M Cost | ID | General Service | Parent-Time-of-Use Opt-in | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inAnnual O&M Cost per MW | ID | General Service | Parent-Time-of-Use Opt-in | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inAnnual Program Administration Cost | ID | General Service | Parent-Time-of-Use Opt-in | Annual Program Administration Cost | $/yr | 15539.513 | 2024 Avista Update |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inCost of Equip + Install | ID | General Service | Parent-Time-of-Use Opt-in | Cost of Equip + Install | $/tech | 0 | 0 |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inCost of Equip + Install (per kW basis) | ID | General Service | Parent-Time-of-Use Opt-in | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inDe-rate | ID | General Service | Parent-Time-of-Use Opt-in | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inNet to Gross Ratio (free ridership) | ID | General Service | Parent-Time-of-Use Opt-in | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inPer Customer Annual Marketing/Recruitment Cost | ID | General Service | Parent-Time-of-Use Opt-in | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | 2024 Avista Update |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inPer Participant Annual Incentive | ID | General Service | Parent-Time-of-Use Opt-in | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inPer kW Annual Incentive | ID | General Service | Parent-Time-of-Use Opt-in | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inProgram Development Cost | ID | General Service | Parent-Time-of-Use Opt-in | Program Development Cost | $/program | 188973.5244 | 2024 Avista Update- WA dev costs are sunk($2 mil), ID costs will be half of WA @ $1mil dev costs |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inProgram Life | ID | General Service | Parent-Time-of-Use Opt-in | Program Life | years | 10 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceParent-Time-of-Use Opt-inProgram Start Year | ID | General Service | Parent-Time-of-Use Opt-in | Program Start Year | year | 2028 | WA; ID Start in 2028: 2024 Avista Update; will change ramp rate after model run |  | General ServiceProgram Start Year | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inSummer DR Event Hours | ID | Large General Service | Parent-Time-of-Use Opt-in | Summer DR Event Hours | hours/year |  |  |  | Large General ServiceSummer DR Event Hours | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inWinter DR Event Hours | ID | Large General Service | Parent-Time-of-Use Opt-in | Winter DR Event Hours | hours/year |  |  |  | Large General ServiceWinter DR Event Hours | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inAnnual O&M Cost | ID | Large General Service | Parent-Time-of-Use Opt-in | Annual O&M Cost | $/participant/year |  |  |  | Large General ServiceAnnual O&M Cost | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inAnnual O&M Cost per MW | ID | Large General Service | Parent-Time-of-Use Opt-in | Annual O&M Cost per MW | $/MW @meter |  |  |  | Large General ServiceAnnual O&M Cost per MW | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inAnnual Program Administration Cost | ID | Large General Service | Parent-Time-of-Use Opt-in | Annual Program Administration Cost | $/yr |  |  |  | Large General ServiceAnnual Program Administration Cost | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inCost of Equip + Install | ID | Large General Service | Parent-Time-of-Use Opt-in | Cost of Equip + Install | $/tech |  |  |  | Large General ServiceCost of Equip + Install | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inCost of Equip + Install (per kW basis) | ID | Large General Service | Parent-Time-of-Use Opt-in | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inDe-rate | ID | Large General Service | Parent-Time-of-Use Opt-in | De-rate | capacity equivalence factor |  |  |  | Large General ServiceDe-rate | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inNet to Gross Ratio (free ridership) | ID | Large General Service | Parent-Time-of-Use Opt-in | Net to Gross Ratio (free ridership) | ratio |  |  |  | Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inPer Customer Annual Marketing/Recruitment Cost | ID | Large General Service | Parent-Time-of-Use Opt-in | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inPer Participant Annual Incentive | ID | Large General Service | Parent-Time-of-Use Opt-in | Per Participant Annual Incentive | $/participant/year |  |  |  | Large General ServicePer Participant Annual Incentive | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inPer kW Annual Incentive | ID | Large General Service | Parent-Time-of-Use Opt-in | Per kW Annual Incentive | $/kW @meter/year |  |  |  | Large General ServicePer kW Annual Incentive | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inProgram Development Cost | ID | Large General Service | Parent-Time-of-Use Opt-in | Program Development Cost | $/program |  |  |  | Large General ServiceProgram Development Cost | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inProgram Life | ID | Large General Service | Parent-Time-of-Use Opt-in | Program Life | years |  |  |  | Large General ServiceProgram Life | Market PotentialID
IDLarge General ServiceParent-Time-of-Use Opt-inProgram Start Year | ID | Large General Service | Parent-Time-of-Use Opt-in | Program Start Year | year |  |  |  | Large General ServiceProgram Start Year | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inSummer DR Event Hours | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Summer DR Event Hours | hours/year |  |  |  | Extra Large General ServiceSummer DR Event Hours | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inWinter DR Event Hours | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Winter DR Event Hours | hours/year |  |  |  | Extra Large General ServiceWinter DR Event Hours | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inAnnual O&M Cost | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Annual O&M Cost | $/participant/year |  |  |  | Extra Large General ServiceAnnual O&M Cost | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inAnnual O&M Cost per MW | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Annual O&M Cost per MW | $/MW @meter |  |  |  | Extra Large General ServiceAnnual O&M Cost per MW | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inAnnual Program Administration Cost | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Annual Program Administration Cost | $/yr |  |  |  | Extra Large General ServiceAnnual Program Administration Cost | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inCost of Equip + Install | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Cost of Equip + Install | $/tech |  |  |  | Extra Large General ServiceCost of Equip + Install | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inCost of Equip + Install (per kW basis) | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | Extra Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inDe-rate | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | De-rate | capacity equivalence factor |  |  |  | Extra Large General ServiceDe-rate | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inNet to Gross Ratio (free ridership) | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Net to Gross Ratio (free ridership) | ratio |  |  |  | Extra Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inPer Customer Annual Marketing/Recruitment Cost | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inPer Participant Annual Incentive | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Per Participant Annual Incentive | $/participant/year |  |  |  | Extra Large General ServicePer Participant Annual Incentive | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inPer kW Annual Incentive | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Per kW Annual Incentive | $/kW @meter/year |  |  |  | Extra Large General ServicePer kW Annual Incentive | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inProgram Development Cost | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Program Development Cost | $/program |  |  |  | Extra Large General ServiceProgram Development Cost | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inProgram Life | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Program Life | years |  |  |  | Extra Large General ServiceProgram Life | Market PotentialID
IDExtra Large General ServiceParent-Time-of-Use Opt-inProgram Start Year | ID | Extra Large General Service | Parent-Time-of-Use Opt-in | Program Start Year | year |  |  |  | Extra Large General ServiceProgram Start Year | Market PotentialID
IDResidentialTime-of-Use Opt-OutSummer DR Event Hours | ID | Residential | Time-of-Use Opt-Out | Summer DR Event Hours | hours/year | 528 | Six hours on-peak period each summer weekday |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialTime-of-Use Opt-OutWinter DR Event Hours | ID | Residential | Time-of-Use Opt-Out | Winter DR Event Hours | hours/year | 528 | Six hours on-peak period each winter weekday too, except for Utah |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialTime-of-Use Opt-OutAnnual O&M Cost | ID | Residential | Time-of-Use Opt-Out | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialTime-of-Use Opt-OutAnnual O&M Cost per MW | ID | Residential | Time-of-Use Opt-Out | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialTime-of-Use Opt-OutAnnual Program Administration Cost | ID | Residential | Time-of-Use Opt-Out | Annual Program Administration Cost | $/yr | 58893.6424 | 2024 Avista Update |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialTime-of-Use Opt-OutCost of Equip + Install | ID | Residential | Time-of-Use Opt-Out | Cost of Equip + Install | $/tech | 0 | 0 |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialTime-of-Use Opt-OutCost of Equip + Install (per kW basis) | ID | Residential | Time-of-Use Opt-Out | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialTime-of-Use Opt-OutDe-rate | ID | Residential | Time-of-Use Opt-Out | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialTime-of-Use Opt-OutNet to Gross Ratio (free ridership) | ID | Residential | Time-of-Use Opt-Out | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialTime-of-Use Opt-OutPer Customer Annual Marketing/Recruitment Cost | ID | Residential | Time-of-Use Opt-Out | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | 2024 Avista Update |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialTime-of-Use Opt-OutPer Participant Annual Incentive | ID | Residential | Time-of-Use Opt-Out | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialTime-of-Use Opt-OutPer kW Annual Incentive | ID | Residential | Time-of-Use Opt-Out | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialTime-of-Use Opt-OutProgram Development Cost | ID | Residential | Time-of-Use Opt-Out | Program Development Cost | $/program | 353347.7202 | 2024 Avista Update |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialTime-of-Use Opt-OutProgram Life | ID | Residential | Time-of-Use Opt-Out | Program Life | years | 10 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialTime-of-Use Opt-OutProgram Start Year | ID | Residential | Time-of-Use Opt-Out | Program Start Year | year | 2028 | 2024 Avista Update |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutSummer DR Event Hours | ID | General Service | Time-of-Use Opt-Out | Summer DR Event Hours | hours/year | 528 | Six hours on-peak period each summer weekday |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutWinter DR Event Hours | ID | General Service | Time-of-Use Opt-Out | Winter DR Event Hours | hours/year | 528 | Six hours on-peak period each winter weekday too, except for Utah |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutAnnual O&M Cost | ID | General Service | Time-of-Use Opt-Out | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutAnnual O&M Cost per MW | ID | General Service | Time-of-Use Opt-Out | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutAnnual Program Administration Cost | ID | General Service | Time-of-Use Opt-Out | Annual Program Administration Cost | $/yr | 23005.4262 | 2024 Avista Update |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutCost of Equip + Install | ID | General Service | Time-of-Use Opt-Out | Cost of Equip + Install | $/tech | 0 | 0 |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutCost of Equip + Install (per kW basis) | ID | General Service | Time-of-Use Opt-Out | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutDe-rate | ID | General Service | Time-of-Use Opt-Out | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutNet to Gross Ratio (free ridership) | ID | General Service | Time-of-Use Opt-Out | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutPer Customer Annual Marketing/Recruitment Cost | ID | General Service | Time-of-Use Opt-Out | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | 2024 Avista Update |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutPer Participant Annual Incentive | ID | General Service | Time-of-Use Opt-Out | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutPer kW Annual Incentive | ID | General Service | Time-of-Use Opt-Out | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutProgram Development Cost | ID | General Service | Time-of-Use Opt-Out | Program Development Cost | $/program | 138027.0364 | 2024 Avista Update |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutProgram Life | ID | General Service | Time-of-Use Opt-Out | Program Life | years | 10 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceTime-of-Use Opt-OutProgram Start Year | ID | General Service | Time-of-Use Opt-Out | Program Start Year | year | 2028 | 0 |  | General ServiceProgram Start Year | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutSummer DR Event Hours | ID | Large General Service | Time-of-Use Opt-Out | Summer DR Event Hours | hours/year |  |  |  | Large General ServiceSummer DR Event Hours | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutWinter DR Event Hours | ID | Large General Service | Time-of-Use Opt-Out | Winter DR Event Hours | hours/year |  |  |  | Large General ServiceWinter DR Event Hours | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutAnnual O&M Cost | ID | Large General Service | Time-of-Use Opt-Out | Annual O&M Cost | $/participant/year |  |  |  | Large General ServiceAnnual O&M Cost | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutAnnual O&M Cost per MW | ID | Large General Service | Time-of-Use Opt-Out | Annual O&M Cost per MW | $/MW @meter |  |  |  | Large General ServiceAnnual O&M Cost per MW | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutAnnual Program Administration Cost | ID | Large General Service | Time-of-Use Opt-Out | Annual Program Administration Cost | $/yr |  |  |  | Large General ServiceAnnual Program Administration Cost | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutCost of Equip + Install | ID | Large General Service | Time-of-Use Opt-Out | Cost of Equip + Install | $/tech |  |  |  | Large General ServiceCost of Equip + Install | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutCost of Equip + Install (per kW basis) | ID | Large General Service | Time-of-Use Opt-Out | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutDe-rate | ID | Large General Service | Time-of-Use Opt-Out | De-rate | capacity equivalence factor |  |  |  | Large General ServiceDe-rate | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutNet to Gross Ratio (free ridership) | ID | Large General Service | Time-of-Use Opt-Out | Net to Gross Ratio (free ridership) | ratio |  |  |  | Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutPer Customer Annual Marketing/Recruitment Cost | ID | Large General Service | Time-of-Use Opt-Out | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutPer Participant Annual Incentive | ID | Large General Service | Time-of-Use Opt-Out | Per Participant Annual Incentive | $/participant/year |  |  |  | Large General ServicePer Participant Annual Incentive | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutPer kW Annual Incentive | ID | Large General Service | Time-of-Use Opt-Out | Per kW Annual Incentive | $/kW @meter/year |  |  |  | Large General ServicePer kW Annual Incentive | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutProgram Development Cost | ID | Large General Service | Time-of-Use Opt-Out | Program Development Cost | $/program |  |  |  | Large General ServiceProgram Development Cost | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutProgram Life | ID | Large General Service | Time-of-Use Opt-Out | Program Life | years |  |  |  | Large General ServiceProgram Life | Market PotentialID
IDLarge General ServiceTime-of-Use Opt-OutProgram Start Year | ID | Large General Service | Time-of-Use Opt-Out | Program Start Year | year |  |  |  | Large General ServiceProgram Start Year | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutSummer DR Event Hours | ID | Extra Large General Service | Time-of-Use Opt-Out | Summer DR Event Hours | hours/year |  |  |  | Extra Large General ServiceSummer DR Event Hours | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutWinter DR Event Hours | ID | Extra Large General Service | Time-of-Use Opt-Out | Winter DR Event Hours | hours/year |  |  |  | Extra Large General ServiceWinter DR Event Hours | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutAnnual O&M Cost | ID | Extra Large General Service | Time-of-Use Opt-Out | Annual O&M Cost | $/participant/year |  |  |  | Extra Large General ServiceAnnual O&M Cost | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutAnnual O&M Cost per MW | ID | Extra Large General Service | Time-of-Use Opt-Out | Annual O&M Cost per MW | $/MW @meter |  |  |  | Extra Large General ServiceAnnual O&M Cost per MW | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutAnnual Program Administration Cost | ID | Extra Large General Service | Time-of-Use Opt-Out | Annual Program Administration Cost | $/yr |  |  |  | Extra Large General ServiceAnnual Program Administration Cost | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutCost of Equip + Install | ID | Extra Large General Service | Time-of-Use Opt-Out | Cost of Equip + Install | $/tech |  |  |  | Extra Large General ServiceCost of Equip + Install | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutCost of Equip + Install (per kW basis) | ID | Extra Large General Service | Time-of-Use Opt-Out | Cost of Equip + Install (per kW basis) | $/kW @meter |  |  |  | Extra Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutDe-rate | ID | Extra Large General Service | Time-of-Use Opt-Out | De-rate | capacity equivalence factor |  |  |  | Extra Large General ServiceDe-rate | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutNet to Gross Ratio (free ridership) | ID | Extra Large General Service | Time-of-Use Opt-Out | Net to Gross Ratio (free ridership) | ratio |  |  |  | Extra Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutPer Customer Annual Marketing/Recruitment Cost | ID | Extra Large General Service | Time-of-Use Opt-Out | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year |  |  |  | Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutPer Participant Annual Incentive | ID | Extra Large General Service | Time-of-Use Opt-Out | Per Participant Annual Incentive | $/participant/year |  |  |  | Extra Large General ServicePer Participant Annual Incentive | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutPer kW Annual Incentive | ID | Extra Large General Service | Time-of-Use Opt-Out | Per kW Annual Incentive | $/kW @meter/year |  |  |  | Extra Large General ServicePer kW Annual Incentive | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutProgram Development Cost | ID | Extra Large General Service | Time-of-Use Opt-Out | Program Development Cost | $/program |  |  |  | Extra Large General ServiceProgram Development Cost | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutProgram Life | ID | Extra Large General Service | Time-of-Use Opt-Out | Program Life | years |  |  |  | Extra Large General ServiceProgram Life | Market PotentialID
IDExtra Large General ServiceTime-of-Use Opt-OutProgram Start Year | ID | Extra Large General Service | Time-of-Use Opt-Out | Program Start Year | year |  |  |  | Extra Large General ServiceProgram Start Year | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inSummer DR Event Hours | ID | GS-EV | Electric Vehicle TOU Opt-in | Summer DR Event Hours | hours/year | 528 | Six hours on-peak period each summer weekday |  | GS-EVSummer DR Event Hours | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inWinter DR Event Hours | ID | GS-EV | Electric Vehicle TOU Opt-in | Winter DR Event Hours | hours/year | 528 | Six hours on-peak period each winter weekday too, except for Utah |  | GS-EVWinter DR Event Hours | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inAnnual O&M Cost | ID | GS-EV | Electric Vehicle TOU Opt-in | Annual O&M Cost | $/participant/year | 0 | 0 |  | GS-EVAnnual O&M Cost | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inAnnual O&M Cost per MW | ID | GS-EV | Electric Vehicle TOU Opt-in | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | GS-EVAnnual O&M Cost per MW | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inAnnual Program Administration Cost | ID | GS-EV | Electric Vehicle TOU Opt-in | Annual Program Administration Cost | $/yr | 23738.424 | 0 |  | GS-EVAnnual Program Administration Cost | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inCost of Equip + Install | ID | GS-EV | Electric Vehicle TOU Opt-in | Cost of Equip + Install | $/tech | 0 | 0 |  | GS-EVCost of Equip + Install | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inCost of Equip + Install (per kW basis) | ID | GS-EV | Electric Vehicle TOU Opt-in | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | GS-EVCost of Equip + Install (per kW basis) | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inDe-rate | ID | GS-EV | Electric Vehicle TOU Opt-in | De-rate | capacity equivalence factor | 1 | 0 |  | GS-EVDe-rate | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inNet to Gross Ratio (free ridership) | ID | GS-EV | Electric Vehicle TOU Opt-in | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | GS-EVNet to Gross Ratio (free ridership) | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inPer Customer Annual Marketing/Recruitment Cost | ID | GS-EV | Electric Vehicle TOU Opt-in | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | 2024 Avista Update |  | GS-EVPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inPer Participant Annual Incentive | ID | GS-EV | Electric Vehicle TOU Opt-in | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | GS-EVPer Participant Annual Incentive | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inPer kW Annual Incentive | ID | GS-EV | Electric Vehicle TOU Opt-in | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | GS-EVPer kW Annual Incentive | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inProgram Development Cost | ID | GS-EV | Electric Vehicle TOU Opt-in | Program Development Cost | $/program | 0 | 0 |  | GS-EVProgram Development Cost | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inProgram Life | ID | GS-EV | Electric Vehicle TOU Opt-in | Program Life | years | 10 | 0 |  | GS-EVProgram Life | Market PotentialID
IDGS-EVElectric Vehicle TOU Opt-inProgram Start Year | ID | GS-EV | Electric Vehicle TOU Opt-in | Program Start Year | year | 2025 | 2024 Avista Update |  | GS-EVProgram Start Year | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inSummer DR Event Hours | ID | LGS-EV | Electric Vehicle TOU Opt-in | Summer DR Event Hours | hours/year | 528 | Six hours on-peak period each summer weekday |  | LGS-EVSummer DR Event Hours | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inWinter DR Event Hours | ID | LGS-EV | Electric Vehicle TOU Opt-in | Winter DR Event Hours | hours/year | 528 | Six hours on-peak period each winter weekday too, except for Utah |  | LGS-EVWinter DR Event Hours | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inAnnual O&M Cost | ID | LGS-EV | Electric Vehicle TOU Opt-in | Annual O&M Cost | $/participant/year | 0 | 0 |  | LGS-EVAnnual O&M Cost | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inAnnual O&M Cost per MW | ID | LGS-EV | Electric Vehicle TOU Opt-in | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | LGS-EVAnnual O&M Cost per MW | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inAnnual Program Administration Cost | ID | LGS-EV | Electric Vehicle TOU Opt-in | Annual Program Administration Cost | $/yr | 5986.0705 | 0 |  | LGS-EVAnnual Program Administration Cost | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inCost of Equip + Install | ID | LGS-EV | Electric Vehicle TOU Opt-in | Cost of Equip + Install | $/tech | 0 | 0 |  | LGS-EVCost of Equip + Install | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inCost of Equip + Install (per kW basis) | ID | LGS-EV | Electric Vehicle TOU Opt-in | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | LGS-EVCost of Equip + Install (per kW basis) | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inDe-rate | ID | LGS-EV | Electric Vehicle TOU Opt-in | De-rate | capacity equivalence factor | 1 | 0 |  | LGS-EVDe-rate | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inNet to Gross Ratio (free ridership) | ID | LGS-EV | Electric Vehicle TOU Opt-in | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | LGS-EVNet to Gross Ratio (free ridership) | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inPer Customer Annual Marketing/Recruitment Cost | ID | LGS-EV | Electric Vehicle TOU Opt-in | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 50 | 2024 Avista Update |  | LGS-EVPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inPer Participant Annual Incentive | ID | LGS-EV | Electric Vehicle TOU Opt-in | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | LGS-EVPer Participant Annual Incentive | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inPer kW Annual Incentive | ID | LGS-EV | Electric Vehicle TOU Opt-in | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | LGS-EVPer kW Annual Incentive | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inProgram Development Cost | ID | LGS-EV | Electric Vehicle TOU Opt-in | Program Development Cost | $/program | 0 | 0 |  | LGS-EVProgram Development Cost | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inProgram Life | ID | LGS-EV | Electric Vehicle TOU Opt-in | Program Life | years | 10 | 0 |  | LGS-EVProgram Life | Market PotentialID
IDLGS-EVElectric Vehicle TOU Opt-inProgram Start Year | ID | LGS-EV | Electric Vehicle TOU Opt-in | Program Start Year | year | 2025 | 2024 Avista Update |  | LGS-EVProgram Start Year | Market PotentialID
IDResidentialPilot-Peak Time RebateSummer DR Event Hours | ID | Residential | Pilot-Peak Time Rebate | Summer DR Event Hours | hours/year | 0 | 4 hours per event, 15-20 events per year. 3 hours per event in PGE, 5 summer and 2 winter events. |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialPilot-Peak Time RebateWinter DR Event Hours | ID | Residential | Pilot-Peak Time Rebate | Winter DR Event Hours | hours/year | 0 | 4 hours per event, 15-20 events per year. 3 hours per event in PGE, 5 summer and 2 winter events. |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialPilot-Peak Time RebateAnnual O&M Cost | ID | Residential | Pilot-Peak Time Rebate | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialPilot-Peak Time RebateAnnual O&M Cost per MW | ID | Residential | Pilot-Peak Time Rebate | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialPilot-Peak Time RebateAnnual Program Administration Cost | ID | Residential | Pilot-Peak Time Rebate | Annual Program Administration Cost | $/yr | 0 | 0 |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialPilot-Peak Time RebateCost of Equip + Install | ID | Residential | Pilot-Peak Time Rebate | Cost of Equip + Install | $/tech | 0 | Assume zero, but would be $470 w tech costs included. Based on PacifiCorp estimate: $270 for PCT, plus $200 for installation |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialPilot-Peak Time RebateCost of Equip + Install (per kW basis) | ID | Residential | Pilot-Peak Time Rebate | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialPilot-Peak Time RebateDe-rate | ID | Residential | Pilot-Peak Time Rebate | De-rate | capacity equivalence factor | 0 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialPilot-Peak Time RebateNet to Gross Ratio (free ridership) | ID | Residential | Pilot-Peak Time Rebate | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialPilot-Peak Time RebatePer Customer Annual Marketing/Recruitment Cost | ID | Residential | Pilot-Peak Time Rebate | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | 0 |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialPilot-Peak Time RebatePer Participant Annual Incentive | ID | Residential | Pilot-Peak Time Rebate | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialPilot-Peak Time RebatePer kW Annual Incentive | ID | Residential | Pilot-Peak Time Rebate | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialPilot-Peak Time RebateProgram Development Cost | ID | Residential | Pilot-Peak Time Rebate | Program Development Cost | $/program | 0 | 0 |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialPilot-Peak Time RebateProgram Life | ID | Residential | Pilot-Peak Time Rebate | Program Life | years | 0 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialPilot-Peak Time RebateProgram Start Year | ID | Residential | Pilot-Peak Time Rebate | Program Start Year | year | 0 | 0 |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServicePilot-Peak Time RebateSummer DR Event Hours | ID | General Service | Pilot-Peak Time Rebate | Summer DR Event Hours | hours/year | 0 | 4 hours per event, 15-20 events per year |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServicePilot-Peak Time RebateWinter DR Event Hours | ID | General Service | Pilot-Peak Time Rebate | Winter DR Event Hours | hours/year | 0 | 4 hours per event, 15-20 events per year |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServicePilot-Peak Time RebateAnnual O&M Cost | ID | General Service | Pilot-Peak Time Rebate | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServicePilot-Peak Time RebateAnnual O&M Cost per MW | ID | General Service | Pilot-Peak Time Rebate | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServicePilot-Peak Time RebateAnnual Program Administration Cost | ID | General Service | Pilot-Peak Time Rebate | Annual Program Administration Cost | $/yr | 0 | 0 |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServicePilot-Peak Time RebateCost of Equip + Install | ID | General Service | Pilot-Peak Time Rebate | Cost of Equip + Install | $/tech | 0 | Assume zero, but would be $470 w tech costs included. Based on PacifiCorp estimate: $270 for PCT, plus $200 for installation |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServicePilot-Peak Time RebateCost of Equip + Install (per kW basis) | ID | General Service | Pilot-Peak Time Rebate | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServicePilot-Peak Time RebateDe-rate | ID | General Service | Pilot-Peak Time Rebate | De-rate | capacity equivalence factor | 0 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServicePilot-Peak Time RebateNet to Gross Ratio (free ridership) | ID | General Service | Pilot-Peak Time Rebate | Net to Gross Ratio (free ridership) | ratio | 0 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServicePilot-Peak Time RebatePer Customer Annual Marketing/Recruitment Cost | ID | General Service | Pilot-Peak Time Rebate | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 0 | 0 |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServicePilot-Peak Time RebatePer Participant Annual Incentive | ID | General Service | Pilot-Peak Time Rebate | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServicePilot-Peak Time RebatePer kW Annual Incentive | ID | General Service | Pilot-Peak Time Rebate | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServicePilot-Peak Time RebateProgram Development Cost | ID | General Service | Pilot-Peak Time Rebate | Program Development Cost | $/program | 0 | 0 |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServicePilot-Peak Time RebateProgram Life | ID | General Service | Pilot-Peak Time Rebate | Program Life | years | 0 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServicePilot-Peak Time RebateProgram Start Year | ID | General Service | Pilot-Peak Time Rebate | Program Start Year | year | 0 | 0 |  | General ServiceProgram Start Year | Market PotentialID
IDResidentialParent-Peak Time RebateSummer DR Event Hours | ID | Residential | Parent-Peak Time Rebate | Summer DR Event Hours | hours/year | 40 | 4 hours per event, 15-20 events per year. 3 hours per event in PGE, 5 summer and 2 winter events. |  | ResidentialSummer DR Event Hours | Market PotentialID
IDResidentialParent-Peak Time RebateWinter DR Event Hours | ID | Residential | Parent-Peak Time Rebate | Winter DR Event Hours | hours/year | 40 | 4 hours per event, 15-20 events per year. 3 hours per event in PGE, 5 summer and 2 winter events. |  | ResidentialWinter DR Event Hours | Market PotentialID
IDResidentialParent-Peak Time RebateAnnual O&M Cost | ID | Residential | Parent-Peak Time Rebate | Annual O&M Cost | $/participant/year | 0 | 0 |  | ResidentialAnnual O&M Cost | Market PotentialID
IDResidentialParent-Peak Time RebateAnnual O&M Cost per MW | ID | Residential | Parent-Peak Time Rebate | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | ResidentialAnnual O&M Cost per MW | Market PotentialID
IDResidentialParent-Peak Time RebateAnnual Program Administration Cost | ID | Residential | Parent-Peak Time Rebate | Annual Program Administration Cost | $/yr | 14858.8212 | 0 |  | ResidentialAnnual Program Administration Cost | Market PotentialID
IDResidentialParent-Peak Time RebateCost of Equip + Install | ID | Residential | Parent-Peak Time Rebate | Cost of Equip + Install | $/tech | 0 | Assume zero, but would be $470 w tech costs included. Based on PacifiCorp estimate: $270 for PCT, plus $200 for installation |  | ResidentialCost of Equip + Install | Market PotentialID
IDResidentialParent-Peak Time RebateCost of Equip + Install (per kW basis) | ID | Residential | Parent-Peak Time Rebate | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | ResidentialCost of Equip + Install (per kW basis) | Market PotentialID
IDResidentialParent-Peak Time RebateDe-rate | ID | Residential | Parent-Peak Time Rebate | De-rate | capacity equivalence factor | 1 | 0 |  | ResidentialDe-rate | Market PotentialID
IDResidentialParent-Peak Time RebateNet to Gross Ratio (free ridership) | ID | Residential | Parent-Peak Time Rebate | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | ResidentialNet to Gross Ratio (free ridership) | Market PotentialID
IDResidentialParent-Peak Time RebatePer Customer Annual Marketing/Recruitment Cost | ID | Residential | Parent-Peak Time Rebate | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | 2024 Avista Update |  | ResidentialPer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDResidentialParent-Peak Time RebatePer Participant Annual Incentive | ID | Residential | Parent-Peak Time Rebate | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | ResidentialPer Participant Annual Incentive | Market PotentialID
IDResidentialParent-Peak Time RebatePer kW Annual Incentive | ID | Residential | Parent-Peak Time Rebate | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | ResidentialPer kW Annual Incentive | Market PotentialID
IDResidentialParent-Peak Time RebateProgram Development Cost | ID | Residential | Parent-Peak Time Rebate | Program Development Cost | $/program | 445675.5015 | 0 |  | ResidentialProgram Development Cost | Market PotentialID
IDResidentialParent-Peak Time RebateProgram Life | ID | Residential | Parent-Peak Time Rebate | Program Life | years | 10 | 0 |  | ResidentialProgram Life | Market PotentialID
IDResidentialParent-Peak Time RebateProgram Start Year | ID | Residential | Parent-Peak Time Rebate | Program Start Year | year | 2028 | 2024 Avista: ID start in 2028 |  | ResidentialProgram Start Year | Market PotentialID
IDGeneral ServiceParent-Peak Time RebateSummer DR Event Hours | ID | General Service | Parent-Peak Time Rebate | Summer DR Event Hours | hours/year | 40 | 4 hours per event, 15-20 events per year |  | General ServiceSummer DR Event Hours | Market PotentialID
IDGeneral ServiceParent-Peak Time RebateWinter DR Event Hours | ID | General Service | Parent-Peak Time Rebate | Winter DR Event Hours | hours/year | 40 | 4 hours per event, 15-20 events per year |  | General ServiceWinter DR Event Hours | Market PotentialID
IDGeneral ServiceParent-Peak Time RebateAnnual O&M Cost | ID | General Service | Parent-Peak Time Rebate | Annual O&M Cost | $/participant/year | 0 | 0 |  | General ServiceAnnual O&M Cost | Market PotentialID
IDGeneral ServiceParent-Peak Time RebateAnnual O&M Cost per MW | ID | General Service | Parent-Peak Time Rebate | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | General ServiceAnnual O&M Cost per MW | Market PotentialID
IDGeneral ServiceParent-Peak Time RebateAnnual Program Administration Cost | ID | General Service | Parent-Peak Time Rebate | Annual Program Administration Cost | $/yr | 1661.9803 | 0 |  | General ServiceAnnual Program Administration Cost | Market PotentialID
IDGeneral ServiceParent-Peak Time RebateCost of Equip + Install | ID | General Service | Parent-Peak Time Rebate | Cost of Equip + Install | $/tech | 0 | Assume zero, but would be $470 w tech costs included. Based on PacifiCorp estimate: $270 for PCT, plus $200 for installation |  | General ServiceCost of Equip + Install | Market PotentialID
IDGeneral ServiceParent-Peak Time RebateCost of Equip + Install (per kW basis) | ID | General Service | Parent-Peak Time Rebate | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | 0 |  | General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDGeneral ServiceParent-Peak Time RebateDe-rate | ID | General Service | Parent-Peak Time Rebate | De-rate | capacity equivalence factor | 1 | 0 |  | General ServiceDe-rate | Market PotentialID
IDGeneral ServiceParent-Peak Time RebateNet to Gross Ratio (free ridership) | ID | General Service | Parent-Peak Time Rebate | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDGeneral ServiceParent-Peak Time RebatePer Customer Annual Marketing/Recruitment Cost | ID | General Service | Parent-Peak Time Rebate | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 60 | 2024 Avista Update |  | General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDGeneral ServiceParent-Peak Time RebatePer Participant Annual Incentive | ID | General Service | Parent-Peak Time Rebate | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | General ServicePer Participant Annual Incentive | Market PotentialID
IDGeneral ServiceParent-Peak Time RebatePer kW Annual Incentive | ID | General Service | Parent-Peak Time Rebate | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | General ServicePer kW Annual Incentive | Market PotentialID
IDGeneral ServiceParent-Peak Time RebateProgram Development Cost | ID | General Service | Parent-Peak Time Rebate | Program Development Cost | $/program | 49849.4399 | 0 |  | General ServiceProgram Development Cost | Market PotentialID
IDGeneral ServiceParent-Peak Time RebateProgram Life | ID | General Service | Parent-Peak Time Rebate | Program Life | years | 10 | 0 |  | General ServiceProgram Life | Market PotentialID
IDGeneral ServiceParent-Peak Time RebateProgram Start Year | ID | General Service | Parent-Peak Time Rebate | Program Start Year | year | 2028 | 2024 Avista: ID start in 2028 |  | General ServiceProgram Start Year | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesSummer DR Event Hours | ID | Large General Service | Variable Peak Pricing Rates | Summer DR Event Hours | hours/year | 40 | Top 40 summer system hours |  | Large General ServiceSummer DR Event Hours | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesWinter DR Event Hours | ID | Large General Service | Variable Peak Pricing Rates | Winter DR Event Hours | hours/year | 40 | Using summer hours except for UT |  | Large General ServiceWinter DR Event Hours | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesAnnual O&M Cost | ID | Large General Service | Variable Peak Pricing Rates | Annual O&M Cost | $/participant/year | 0 | 0 |  | Large General ServiceAnnual O&M Cost | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesAnnual O&M Cost per MW | ID | Large General Service | Variable Peak Pricing Rates | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | Large General ServiceAnnual O&M Cost per MW | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesAnnual Program Administration Cost | ID | Large General Service | Variable Peak Pricing Rates | Annual Program Administration Cost | $/yr | 15569.5434 | 0 |  | Large General ServiceAnnual Program Administration Cost | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesCost of Equip + Install | ID | Large General Service | Variable Peak Pricing Rates | Cost of Equip + Install | $/tech | 0 | No equipment cost because assuming they have their own technology (like a Energy Management System etc) to control their processes |  | Large General ServiceCost of Equip + Install | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesCost of Equip + Install (per kW basis) | ID | Large General Service | Variable Peak Pricing Rates | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | Currently zero, but $360/kW if tech costs included. Based on Auto-DR tech enablement costs. $300/kW is incentive level offered by SCE for Auto-DR participants, and is expected to cover a large fraction of costs. 20% adder included to recognize some additional expenses on the part of the customer. |  | Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesDe-rate | ID | Large General Service | Variable Peak Pricing Rates | De-rate | capacity equivalence factor | 1 | 0 |  | Large General ServiceDe-rate | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesNet to Gross Ratio (free ridership) | ID | Large General Service | Variable Peak Pricing Rates | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesPer Customer Annual Marketing/Recruitment Cost | ID | Large General Service | Variable Peak Pricing Rates | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 200 | Assumed 4X Residential recruitment costs of $50 |  | Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesPer Participant Annual Incentive | ID | Large General Service | Variable Peak Pricing Rates | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | Large General ServicePer Participant Annual Incentive | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesPer kW Annual Incentive | ID | Large General Service | Variable Peak Pricing Rates | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | Large General ServicePer kW Annual Incentive | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesProgram Development Cost | ID | Large General Service | Variable Peak Pricing Rates | Program Development Cost | $/program | 15569.5434 | 0 |  | Large General ServiceProgram Development Cost | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesProgram Life | ID | Large General Service | Variable Peak Pricing Rates | Program Life | years | 10 | 0 |  | Large General ServiceProgram Life | Market PotentialID
IDLarge General ServiceVariable Peak Pricing RatesProgram Start Year | ID | Large General Service | Variable Peak Pricing Rates | Program Start Year | year | 2026 | Metering capability exists in this class, but need 2 years before program can be implemented and ramp up. |  | Large General ServiceProgram Start Year | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesSummer DR Event Hours | ID | Extra Large General Service | Variable Peak Pricing Rates | Summer DR Event Hours | hours/year | 40 | Top 40 summer system hours |  | Extra Large General ServiceSummer DR Event Hours | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesWinter DR Event Hours | ID | Extra Large General Service | Variable Peak Pricing Rates | Winter DR Event Hours | hours/year | 40 | Using summer hours except for UT |  | Extra Large General ServiceWinter DR Event Hours | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesAnnual O&M Cost | ID | Extra Large General Service | Variable Peak Pricing Rates | Annual O&M Cost | $/participant/year | 0 | 0 |  | Extra Large General ServiceAnnual O&M Cost | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesAnnual O&M Cost per MW | ID | Extra Large General Service | Variable Peak Pricing Rates | Annual O&M Cost per MW | $/MW @meter | 0 | 0 |  | Extra Large General ServiceAnnual O&M Cost per MW | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesAnnual Program Administration Cost | ID | Extra Large General Service | Variable Peak Pricing Rates | Annual Program Administration Cost | $/yr | 7932.4396 | 0 |  | Extra Large General ServiceAnnual Program Administration Cost | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesCost of Equip + Install | ID | Extra Large General Service | Variable Peak Pricing Rates | Cost of Equip + Install | $/tech | 0 | 0 |  | Extra Large General ServiceCost of Equip + Install | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesCost of Equip + Install (per kW basis) | ID | Extra Large General Service | Variable Peak Pricing Rates | Cost of Equip + Install (per kW basis) | $/kW @meter | 0 | Currently zero, but $360/kW if tech costs included. Based on Auto-DR tech enablement costs. $300/kW is incentive level offered by SCE for Auto-DR participants, and is expected to cover a large fraction of costs. 20% adder included to recognize some additional expenses on the part of the customer. |  | Extra Large General ServiceCost of Equip + Install (per kW basis) | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesDe-rate | ID | Extra Large General Service | Variable Peak Pricing Rates | De-rate | capacity equivalence factor | 1 | 0 |  | Extra Large General ServiceDe-rate | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesNet to Gross Ratio (free ridership) | ID | Extra Large General Service | Variable Peak Pricing Rates | Net to Gross Ratio (free ridership) | ratio | 1 | 0 |  | Extra Large General ServiceNet to Gross Ratio (free ridership) | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesPer Customer Annual Marketing/Recruitment Cost | ID | Extra Large General Service | Variable Peak Pricing Rates | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | 400 | Assumed 2X Large C&I recruitment costs |  | Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesPer Participant Annual Incentive | ID | Extra Large General Service | Variable Peak Pricing Rates | Per Participant Annual Incentive | $/participant/year | 0 | Incentive built into rate design |  | Extra Large General ServicePer Participant Annual Incentive | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesPer kW Annual Incentive | ID | Extra Large General Service | Variable Peak Pricing Rates | Per kW Annual Incentive | $/kW @meter/year | 0 | 0 |  | Extra Large General ServicePer kW Annual Incentive | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesProgram Development Cost | ID | Extra Large General Service | Variable Peak Pricing Rates | Program Development Cost | $/program | 7932.4396 | 0 |  | Extra Large General ServiceProgram Development Cost | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesProgram Life | ID | Extra Large General Service | Variable Peak Pricing Rates | Program Life | years | 10 | 0 |  | Extra Large General ServiceProgram Life | Market PotentialID
IDExtra Large General ServiceVariable Peak Pricing RatesProgram Start Year | ID | Extra Large General Service | Variable Peak Pricing Rates | Program Start Year | year | 2026 | Metering capability exists in this class, but need 2 years before program can be implemented and ramp up. |  | Extra Large General ServiceProgram Start Year | Market PotentialID

## Change Log
Program | Input | Original Value | Original Source | New Value | New Source | Notes | Status | Update Location | Link | Meeting Notes
DLC Central AC | Program Start Year | 2022 | n/a | 2024 | Avista |  | Approved | DLC Central AC'!F35 | Go To Update
DLC Smart Thermostats - Cooling | Program Start Year | 2022 | n/a | 2024 | Avista |  | Approved | DLC Smart Thermostats - Cooling'!F35 | Go To Update
DLC Smart Thermostats - Heating | Program Start Year | 2022 | n/a | 2025 | Avista |  | Approved | DLC Smart Thermostats - Heating'!F35 | Go To Update
Grid-Interactive WH (CTA-2045) | Program Start Year | 2022 | n/a | 2023 | Avista |  | Approved | CTA-2045 WH'!F35 | Go To Update
Ancillary Cooling | Program Start Year | 2022 | n/a | 2024 | Avista | Same as Smart Tstats-Cooling/Central AC DLC | Approved | Ancillary Cooling'!F35 | Go To Update
Ancillary Heating | Program Start Year | 2022 | n/a | 2025 | Avista | Same as Smart Tstats-Heating | Approved | Ancillary Heating'!F35 | Go To Update
DLC Electric Vehicle Charging | Program Start Year | 2024 | n/a | 2025 | n/a | Shifted out one year to keep the 2 year delay in program start. Is this still applicable? | Do not update | DLC Electric Vehicle Charging'!F35 | Go To Update
Ancillary EV | Program Start Year | 2024 | n/a | 2025 | n/a | Same as DLC EV Charging | Do not update | Ancillary EV'!F35 | Go To Update
All programs not listed above | Program Start Year | 2022 | n/a | 2023 | n/a | Shift in base year | Approved | n/a
Electric Vehicle TOU Opt-In | All | n/a | n/a | n/a | Avista | *Slow ramp for EV TOU Zeroed out Dev costs | Approved | n/a
CTA-2045 Water Heater | Per Customer Summer Peak Reduction (kW) | 0.5 | NWPC Electric Resistance Grid-Ready Summer/Winter Impact | See table to the right. We are breaking out the program to reflect the different impacts by equipment type, applying the same forecast as the EE study. | BPA 2018 | Applies to winter impacts as well. | Approved | CTA-2045 ERWH'!F14 | Go To Update
DLC Central AC | Per Customer Summer Peak Reduction (kW) | 0.5 | NWPC DLC Switch cooling assumption (east) | 0.86084 | ID Power, 2020 | 1.01 in 2019. ID only? Share with Kelly | Do not update | DLC Central AC'!H14 | Go To Update
DLC Central AC | Summer DR Event Hours | 50 | Current PC Cool Keeper program allows for max 100 hours of curtailment. | 60 | ID Power, 2020 | ID Only? | Not needed for scope. Table for reporting. | DLC Central AC'!H29 | Go To Update
DLC Central AC | Per Participant Annual Incentive | 20 | $20 is the incentive level per participating unit. No. of units per average participant is 1.059 | 20 | ID Power, 2020 | $5 monthly credit- unclear if this implies only months where event is called, in which case $20-30 is similar --> Source Update only | Approved | DLC Central AC'!H33 | Go To Update
DLC Smart Thermostats - Cooling | Per Customer Summer Peak Reduction (%) | 0.5 | NWPC DLC Switch cooling assumption (east)- Thermostat impact was 1.27 kW but didn't seem right so we defaulted to DLC Central AC | BYOT: Summer- 0.82 (30%) Winter- 0.83 (31%) DI: Summer- 0.94 (30%) Winter- 1.63 (41%) | PGE (OR) 2019-20 Evaluation | Applies to winter impacts as well. We may want to take a look at the forecast by end use and see what seems more reasonable. Share with Kelly | Do not update | DLC Smart Thermostats - Cooling'!F14 | Go To Update
| Per Customer Summer Peak Reduction (%) | 0.5 | NWPC DLC Switch cooling assumption (east)- Thermostat impact was 1.27 kW but didn't seem right so we defaulted to DLC Central AC | 2.68 or 25.8% 2.63 or 10.17% 2.68 or 15.88% | RTF "Residential Connected Thermostats DR Workbook" 2019 | All for HZ2-CZ2 Summer Afternoon Winter Morning Winter Afternoon
Third Party Curtailment | Per Customer Summer Peak Reduction (%) | 21% |  |  |  | See impacts in research file Share with Kelly | Question--> was there an RFP for a third party program? If so, can we see some of the proposals for reference?
Electric Vehicle TOU Opt-In | Participation |  |  |  |  | Keep forecast stagnant or expand? | Limit to EV forecast
Ancillary Third Party Curtailment | Participation | 4.4% | Adjusting by applying a general EMS saturation for commercial segments. | 4.033% | Adjusting by applying the 2020 EE potential study EMS saturation for commercial segments, weighted by segment size. | Updated to pull in weighting from the previous EE study. EMS saturations have not been finalized yet in the 2022 EE study. |  | Ancillary Third Party'!F7 | Go To Update
Variable Peak Pricing / Peak Time Rebate | New Program |  |  |  |  | Replaced Residential and General Service VPP with PTR, based on pilot program and PG&E. | Approved
Peak Time Rebate | [5 empty] | Will the program be revenue neutral? Meaning no kWh incentive is modeled.
New pilots | Add pilot programs as separate small programs |  |  |  |  | Dev costs in pilot only. Starts in 2024. Parents start in 2027. | Approved
EV TOU | All |  |  |  |  | Added customer classes specific to EV forecasts. Participation will be in terms of EVs. | Approved
EV DLC | Peak Impact | 0.5 kW | Avista Estimate. | 75% | Avista 2019 EVSE report | If we change the customer class to the EV-specific ones, the 0.5 kW impact is 69%. We can update that to the 75% and align specifically with the EV customer base. | Approved
EV DLC | EQ cost | 700 | Avista Estimate. | 1766 | Avista 2019 EVSE report | Cost of lvl 2 residential non-networked charger. Not sure where the original Avista assumptions came from. Table also includes commercial charger costs, if we want to add the GS chargers as an option. | Approved
EV DLC | Customer Class | Residential |  |  |  | Should we expand to other customer classes? | Approved
EV TOU | Participation | 8-12.5% | Target participation in yr 1 | 50% | DTE study shows achieving 2500 participants in 3 years, with similar EV customer base size |  | Approved
EV TOU | Ramp | 1 | Existing program | 3 | DTE ramp | Need to check that yr 1 participation is in alignment with current enrollment | Approved
EV TOU | Question on Costs |  |  |  |  | DTE offers a $2500 incentive for charger installation with its own meter. Would Avista offer such an incentive for the rate, or only the DLC? Current DLC incentive is 700/1766 | No incentive for EQ
EV TOU | Hours | 528 | PAC | 1232 | DTE EV-TOU | Shifted on-peak window to match residential circuit load (9 am to 11 PM). | Approved
EV TOU | Peak Impact | 0.2-2.1% | Brattle/PAC 2019 | 7% | estimate using DTE rate differential and Brattle TOU analysis | Currently assuming the same for both seasons and all customer classes | Approved
EV TOU | Start Year | 2023 |  | 2024 |  | Should this program start in 2023 for all classes or 2024 for the res and XL? Originally we had it starting in 2023 for GS and LGS. | Approved
EV TOU | Classes | Res, GS, LGS, ELGS | Previous study | GS, LGS |  | From "Avista Program Input Updates-LH.xlsx" |  |  |  | LT 04232024
EV TOU | Program ramp up period | 3 | Previous study | 5 |  | From "Avista Program Input Updates-LH.xlsx" |  | Electric Vehicle TOU Opt-In'!F8 | Go To Update | LT 04182024
EV TOU | Program ramp up period | 3 | Previous study | 5 |  | From "Avista Program Input Updates-LH.xlsx" |  | Electric Vehicle TOU Opt-In'!F46 | Go To Update | LT 04182024
EV TOU | Per Customer Annual Marketing/Recruitment Cost | 60 | Previous study | 50 |  | From "Avista Program Input Updates-LH.xlsx" |  | Electric Vehicle TOU Opt-In'!F23 | Go To Update | LT 04222024
EV TOU | Per Customer Annual Marketing/Recruitment Cost | 60 | Previous study | 50 |  | From "Avista Program Input Updates-LH.xlsx" |  | Electric Vehicle TOU Opt-In'!F61 | Go To Update | LT 04222024
EV TOU | Per Customer Summer Peak Reduction (%) | 7% | Previous study | 100% |  | From "Avista Program Input Updates-LH.xlsx" |  | Electric Vehicle TOU Opt-In'!F13 | Go To Update | LT 04232024
EV TOU | Per Customer Summer Peak Reduction (%) | 7% | Previous study | 100% |  | From "Avista Program Input Updates-LH.xlsx" |  | Electric Vehicle TOU Opt-In'!F51 | Go To Update | LT 04232024
EV TOU | Steady State Participation Rate (GS) | 50.9% | Previous study | 20% |  | From "Avista Program Input Updates-LH.xlsx" |  | Electric Vehicle TOU Opt-In'!F7 | Go To Update | LT 04232024
EV TOU | Steady State Participation Rate (LGS) | 50.9% | Previous study | 10% |  | From "Avista Program Input Updates-LH.xlsx" |  | Electric Vehicle TOU Opt-In'!F45 | Go To Update | LT 04232024
DLC Electric Vehicle Charging | Classes | Res, GS | Previous study | Res |  | From "Avista Program Input Updates-LH.xlsx" |  |  |  | LT 04232024: delete GS
DLC Electric Vehicle Charging | Ramp rate? |  |  |  |  | From "Avista Program Input Updates-LH.xlsx" |  |  |  | LT 04232024
DLC Electric Vehicle Charging | State | WA, ID | Previous study | WA |  | From "Avista Program Input Updates-LH.xlsx" |  |  |  | LT 04232024: delete ID
DLC Electric Vehicle Charging | Program Start Year | 2024 | Previous study | 2025 |  | From "Avista Program Input Updates-LH.xlsx" |  | DLC Electric Vehicle Charging'!F35 | Go To Update | LT 04222024
DLC Electric Vehicle Charging | Per Customer Summer Peak Reduction (%) | 75% | Previous study | 90% |  | From "Avista Program Input Updates-LH.xlsx" |  | DLC Electric Vehicle Charging'!F13 | Go To Update | LT 04182024
DLC Electric Vehicle Charging | Per Customer Summer Peak Reduction (%) | 75% | Previous study | 90% |  | From "Avista Program Input Updates-LH.xlsx" |  | DLC Electric Vehicle Charging'!F15 | Go To Update | LT 04182024
DLC Electric Vehicle Charging | Steady State Participation Rate | 15% | Previous study | 20% |  | From "Avista Program Input Updates-LH.xlsx" |  | DLC Electric Vehicle Charging'!F7 | Go To Update | LT 04182024: only updated WA
DLC Electric Vehicle Charging | Per Customer Annual Marketing/Recruitment Cost | 50 | Previous study | 350 |  | From "Avista Program Input Updates-LH.xlsx" |  | DLC Electric Vehicle Charging'!F23 | Go To Update | LT 04222024: only updated WA; comments unclear
DLC Electric Vehicle Charging | Per Participant Annual Incentive | 36 | Previous study | 60 |  | From "Avista Program Input Updates-LH.xlsx" |  | DLC Electric Vehicle Charging'!F7 | Go To Update | LT 04222024: only updated WA; comments unclear
DLC Electric Vehicle Charging | Annual Program Administration Cost | 25786.8986 | Previous study | 34382.5315 |  | From "Avista Program Input Updates-LH.xlsx" |  | DLC Electric Vehicle Charging'!F21 | Go To Update | LT 04232024
DLC Electric Vehicle Charging | Annual O&M Cost | 300 | Previous study | 45 |  | From "Avista Program Input Updates-LH.xlsx" |  | DLC Electric Vehicle Charging'!F24 | Go To Update | LT 04232024
Parent TOU Opt-in | Classes | Res, GS, LGS, ELGS | Previous study | Res, GS |  | From "Avista Program Input Updates-LH.xlsx" |  |  |  | LT 04232024
Parent TOU Opt-in | Ramp rate? |  |  |  |  | From "Avista Program Input Updates-LH.xlsx" |  |  |  | LT 04232024
Parent TOU Opt-in | Admin Costs and Asmptns | values for Res, GS, LGS, ELGS | Previous study | set values for LGS and ELGS to zero |  | From "Avista Program Input Updates-LH.xlsx" |  | Admin Costs and Asmptns.'!A56 | Go To Update | LT 04232024
Parent TOU Opt-in | Admin Costs and Asmptns (Total Admin Cost) | 75000 | Previous study | 100000 |  | From "Avista Program Input Updates-LH.xlsx" |  | Admin Costs and Asmptns.'!A19 | Go To Update | LT 04232024
Parent TOU Opt-in | Admin Costs and Asmptns (Development Cost) | 75000 | Previous study | 1000000 |  | From "Avista Program Input Updates-LH.xlsx" |  | Admin Costs and Asmptns.'!A19 | Go To Update | LT 04232024
Parent TOU Opt-in | Per Customer Summer Peak Reduction (%) | 5.7% | Previous study | 4% |  | From "Avista Program Input Updates-LH.xlsx" |  | Parent-Time-of-Use Opt-In'!F13 | Go To Update | LT 04182024
Parent TOU Opt-in | Per Customer Winter Peak Reduction (%) | 2.85% | Previous study | 1.5% |  | From "Avista Program Input Updates-LH.xlsx" |  | Parent-Time-of-Use Opt-In'!F15 | Go To Update | LT 04182024
Parent TOU Opt-in | Program Start Year | 2024 | Previous study | 2025 |  |  |  | Parent-Time-of-Use Opt-In'!F35 | Go To Update | LT 04262024
Parent TOU Opt-in | Program Start Year | 2024 | Previous study | 2025 |  |  |  | Parent-Time-of-Use Opt-In'!F75 | Go To Update | LT 04262024
Parent TOU Opt-in | Program Start Year | 2024 | Previous study | 2028 |  | From "Avista Program Input Updates-LH.xlsx" |  | Parent-Time-of-Use Opt-In'!H35 | Go To Update | LT 04182024
Parent TOU Opt-in | Program Start Year | 2024 | Previous study | 2028 |  | From "Avista Program Input Updates-LH.xlsx" |  | Parent-Time-of-Use Opt-In'!H75 | Go To Update | LT 04182024
Parent TOU Opt-in | Steady State Participation Rate | 13% | Previous study | 7% |  | From "Avista Program Input Updates-LH.xlsx" |  | Parent-Time-of-Use Opt-In'!F7 | Go To Update | LT 04192024
Parent TOU Opt-in | Steady State Participation Rate | 13% | Previous study | 7% |  | From "Avista Program Input Updates-LH.xlsx" |  | Parent-Time-of-Use Opt-In'!F47 | Go To Update | LT 04192024
Parent TOU Opt-in | Per Customer Annual Marketing/Recruitment Cost | 50 | Previous study | 60 |  | From "Avista Program Input Updates-LH.xlsx" |  | Parent-Time-of-Use Opt-In'!F23 | Go To Update | LT 04232024
Parent TOU Opt-in | Per Customer Annual Marketing/Recruitment Cost | $60, $72 | Previous study | 60 |  | From "Avista Program Input Updates-LH.xlsx" |  | Parent-Time-of-Use Opt-In'!F23 | Go To Update | LT 04232024
TOU Opt-out | Classes | Res, GS, LGS, ELGS | Previous study | Res, GS |  | From "Avista Program Input Updates-LH.xlsx" |  |  |  | LT 04232024
TOU Opt-out | Admin Costs and Asmptns | values for Res, GS, LGS, ELGS | Previous study | set values for LGS and ELGS to zero |  | From "Avista Program Input Updates-LH.xlsx" |  | Admin Costs and Asmptns.'!A56 | Go To Update | LT 04232024
TOU Opt-out | Admin Costs and Asmptns (Total Admin Cost) | 75000 | Previous study | 100000 |  | From "Avista Program Input Updates-LH.xlsx" |  | Admin Costs and Asmptns.'!A19 | Go To Update | LT 04232024
TOU Opt-out | Admin Costs and Asmptns (Development Cost) | 75000 | Previous study | 1500000 |  | From "Avista Program Input Updates-LH.xlsx" |  | Admin Costs and Asmptns.'!A19 | Go To Update | LT 04232024
TOU Opt-out | Per Customer Summer Peak Reduction (%) | 3.4% | Previous study | 1.5% |  | From "Avista Program Input Updates-LH.xlsx" |  | Time-of-Use Opt-Out'!F13 | Go To Update | LT 04192024
TOU Opt-out | Per Customer Winter Peak Reduction (%) | 1.7% | Previous study | 0.2% |  | From "Avista Program Input Updates-LH.xlsx" |  | Time-of-Use Opt-Out'!F15 | Go To Update | LT 04192024
TOU Opt-out | Steady State Participation Rate | 74% | Previous study | 20% |  | From "Avista Program Input Updates-LH.xlsx" |  | Time-of-Use Opt-Out'!F7 | Go To Update | LT 04192024
TOU Opt-out | Steady State Participation Rate | 74% | Previous study | 20% |  | From "Avista Program Input Updates-LH.xlsx" |  | Time-of-Use Opt-Out'!F47 | Go To Update | LT 04192024
TOU Opt-out | Per Customer Annual Marketing/Recruitment Cost | 50 | Previous study | 60 |  | From "Avista Program Input Updates-LH.xlsx" |  | Time-of-Use Opt-Out'!F23 | Go To Update | LT 04232024
TOU Opt-out | Per Customer Annual Marketing/Recruitment Cost | $60, $72 | Previous study | 60 |  | From "Avista Program Input Updates-LH.xlsx" |  | Time-of-Use Opt-Out'!F63 | Go To Update | LT 04232024
TOU Opt-out | Program Start Year | 2024 | Previous study | 2025 |  |  |  | Time-of-Use Opt-Out'!F35 | Go To Update | LT 04262024
Electric Vehicle TOU Opt-In | Program Start Year | 2023 | Previous study | 2025 |  |  |  | Electric Vehicle TOU Opt-In'!F35 | Go To Update | LT 04262024
Electric Vehicle TOU Opt-In | Program Start Year | 2023 | Previous study | 2025 |  |  |  | Electric Vehicle TOU Opt-In'!F75 | Go To Update | LT 04262024
Parent-Peak Time Rebate | Ramp rate? |  |  |  |  | From "Avista Program Input Updates-LH.xlsx" |  |  |  | LT 04232024
Parent-Peak Time Rebate | Program Start Year | 2024 | Previous study | 2025 |  | From "Avista Program Input Updates-LH.xlsx" |  | Parent-Peak Time Rebate'!F35 | Go To Update | LT 04262024
Parent-Peak Time Rebate | Program Start Year | 2024 | Previous study | 2028 |  | From "Avista Program Input Updates-LH.xlsx" |  | Parent-Peak Time Rebate'!H35 | Go To Update | LT 04232024
Parent-Peak Time Rebate | Per kWh Annual Incentive | 0 | Previous study | 0.4 |  | From "Avista Program Input Updates-LH.xlsx" |  | Parent-Peak Time Rebate'!F32 | Go To Update | LT 04232024
Parent-Peak Time Rebate | Per kWh Annual Incentive | 0 | Previous study | 0.4 |  | From "Avista Program Input Updates-LH.xlsx" |  | Parent-Peak Time Rebate'!F72 | Go To Update | LT 04232024
Parent-Peak Time Rebate | Admin Costs and Asmptns (Total Admin Cost) | 75000 | Previous study | 50000 |  | From "Avista Program Input Updates-LH.xlsx" |  | Admin Costs and Asmptns.'!A22 | Go To Update | LT 04232024
Parent-Peak Time Rebate | Admin Costs and Asmptns (Development Cost) | 75000 | Previous study | 1500000 |  | From "Avista Program Input Updates-LH.xlsx" |  | Admin Costs and Asmptns.'!A22 | Go To Update | LT 04232024
Parent-Peak Time Rebate | Per Customer Annual Marketing/Recruitment Cost | 50 | Previous study | 60 |  | From "Avista Program Input Updates-LH.xlsx" |  | Parent-Peak Time Rebate!F23 | Go To Update | LT 04232024
Parent-Peak Time Rebate | Per Customer Annual Marketing/Recruitment Cost | 50 | Previous study | 60 |  | From "Avista Program Input Updates-LH.xlsx" |  | Parent-Peak Time Rebate!F63 | Go To Update | LT 04232024
Parent-CTA-2045 HPWH | State | WA, ID | Previous study | WA |  | From "Avista Program Input Updates-LH.xlsx" |  |  |  | LT 04242024
Parent-CTA-2045 HPWH | Ramp rate? |  | Previous study |  |  | From "Avista Program Input Updates-LH.xlsx" |  |  |  | LT 04242024
Parent-CTA-2045 HPWH | Summer DR Event Hours | 75 | Previous study | 210 |  | From "Avista Program Input Updates-LH.xlsx" |  | Parent-CTA-2045 HPWH!F29 | Go To Update | LT 04242024
Parent-CTA-2045 HPWH | Winter DR Event Hours | 75 | Previous study | 210 |  | From "Avista Program Input Updates-LH.xlsx" |  | Parent-CTA-2045 HPWH!F30 | Go To Update | LT 04242024
DLC Smart Thermostats - Cooling | Steady State Participation Rate | 20% | Previous study | 10% |  | From "Avista Program Input Updates-LH.xlsx" |  | DLC Smart Thermostats - Cooling!F47 | Go To Update | LT 04242024
DLC Smart Thermostats - Cooling | Admin Costs and Asmptns (Development Cost) | 75000 | Previous study | 350000 |  | From "Avista Program Input Updates-LH.xlsx" |  | Admin Costs and Asmptns.'!A17 | Go To Update | LT 04242024
DLC Smart Thermostats - Cooling | Annual O&M Cost | 44 | Previous study | 164 |  | From "Avista Program Input Updates-LH.xlsx" |  | DLC Smart Thermostats - Cooling!F24 | Go To Update | LT 04242024
Third Party Contracts | Classes | GS, LGS, Ex LGS | Previous study | LGS, EX LGS |  | From "Avista Program Input Updates-LH.xlsx" |  |  |  | LT 04242024
Third Party Contracts | Steady State Participation Rate | 15%, 22% | Previous study | 15% |  | From "Avista Program Input Updates-LH.xlsx" |  | Third Party Contracts!F7 | Go To Update | LT 04242024
Ancillary EV | Program Start Year | 2024 | Previous study | 2025 |  |  |  | Ancillary EV!F35 | Go To Update | LT 04262024
Ancillary EV | Program Start Year | 2024 | Previous study | 2025 |  |  |  | Ancillary EV!F75 | Go To Update | LT 04262024

## DLC Central AC
| Program Option: | DLC Central AC |  | Market PotentialWA | Market PotentialID |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes | Residential | #REF! | #REF!
|  |  |  | State | State |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  | Large General Service | #REF! | #REF!
| ParticipationRate | [5 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 10% | 10% | NWPC DLC Switch cooling assumption- 5 yr ramp rate | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 5 | 5 |  | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 1% | 1% |  | General Service | #REF! | #REF!
[7 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [5 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential |  |  |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential | 0.5 | 0.5 | NWPC DLC Switch cooling assumption (east) | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential |  |  |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | 43294.5186 | 24949.3718 |  |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | - | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | 51953.4223 | 29939.2462 | Share of Cost as noted in table at right |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential | - | -
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 60 | 60 | Utah $50, All others $60 (20% higher) |  |  |  | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 13 | 13 | Assume 5% of equipment + install costs. |  |  |  | 90000
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | 0 |  |  |  |  | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 260 | 260 | $100 installation cost. Idaho Power at 10,000 quantity pays $160 per switch. It's believed Avista volumes would be the same or less per order, making the cost $160 or greater. |  |  |  | 75000
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | 0 | [5 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | 0 |  |  |  |  | Residential | 57.73% | 33.27%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 50 | 50 | Current PC Cool Keeper program allows for max 100 hours of curtailment. |  |  |  | General Service | 5.521% | 3.487%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 0 | 0 |  |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential | 0 | 0 |  |  |  |  | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0 | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 20 | 20 | $20 is the incentive level per participating unit. No. of units per average participant is 1.059. Aligns with ID Power rebate. |  |  |  | Total | 63.25% | 36.75% | 100%
ResidentialProgram Life | Program Life | years | Residential | 8 | 8
ResidentialProgram Start Year | Program Start Year | year | Residential | 2026 | 2026
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1 | 1
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1 | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 10% | 10% | NWPC DLC Switch cooling assumption- 5 yr ramp rate
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 5 | 5
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1% | 1%
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service |  |  |  | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 1.25 | 1.25 | NWPC DLC Switch cooling assumption (East) | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service |  |  |  | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | 4140.8857 | 2615.2239
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | - | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | 4969.0628 | 3138.2687 | Share of Cost as noted in table at right
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | - | -
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 75 | 75 | 25% Higher than Residential
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 13 | 13 | Assume 5% of equipment + install costs.
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0 | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 260 | 260 | $100 installation cost. Idaho Power at 10,000 quantity pays $160 per switch. It's believed Avista volumes would be the same or less per order, making the cost $160 or greater.
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0 | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0 | 0
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 50 | 50 | Current PC Cool Keeper program allows for max 100 hours of curtailment.
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | 0 | 0
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0 | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0 | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 38 | 38 | Assumed participants have less than 5.5 tons of AC unit. Incentive level provided by PacifiCorp.
General ServiceProgram Life | Program Life | years | General Service | 8 | 8
General ServiceProgram Start Year | Program Start Year | year | General Service | 2026 | 2026
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1 | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1 | 1

## DLC Smart Thermostats - Cooling
| Program Option: | DLC Smart Thermostats - Cooling |  | Market PotentialWA | Market PotentialID |  | *Same Impacts as DLC CAC | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes |  | Residential | #REF! | #REF!
|  |  |  | State | State |  |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  |  | Large General Service | #REF! | #REF!
| ParticipationRate | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 20% | 20% | NWPC Smart Thermostat cooling assumption- 5 yr ramp rate |  | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 5 | 5 |  |  | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 1% | 1% |  |  | General Service | #REF! | #REF!
[8 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 0% | 0%
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential |  |  |  |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential | 0.5 | 0.5 | NWPC DLC Switch cooling assumption (east)- Thermostat impact was 1.27 kW but didn't seem right so we defaulted to DLC Central AC |  | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential |  |  |  |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | 202041.0869 | 116430.4017 | Share of Cost as noted in table at right |  |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | - | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | 51953.4223 | 29939.2462 | [5 empty] | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 60 | 60 | Utah $50, All others $60 (20% higher) |  |  |  |  | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 164 | 164 | 2024 Avista Update: $44 + $10/month fee per tstat | Pacificorp assumes 5% of equipment+install costs |  |  |  | 90000
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | 0 | [5 empty] | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 0 | 0 | Bring Your Own Thermostat program |  |  |  |  | 350000 | 2024 Avista Update: + $100,000 internal Avista cost
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | 0 | [6 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | 0 | [5 empty] | Residential | 57.73% | 33.27%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 36 | 36 | 2016 M&V Report Event Hours |  |  |  |  | General Service | 5.521% | 3.487%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | [7 empty] | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential |  | 0 | [5 empty] | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0 | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 20 | 20 | Assume $20 per year per system, same as CAC DLC. |  |  |  |  | Total | 63.25% | 36.75% | 100%
ResidentialProgram Life | Program Life | years | Residential | 10 | 10
ResidentialProgram Start Year | Program Start Year | year | Residential | 2026 | 2026
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1 | 1
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1 | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 10% | 10% | 2024 Avista Update | NWPC Smart Thermostat cooling assumption- 5 yr ramp rate
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 5 | 5
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1% | 1%
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 0% | 0%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service |  |  |  |  | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 1.25 | 1.25 | NWPC DLC Switch cooling assumption (East) |  | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service |  |  |  |  | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | 19324.1332 | 12204.3782 | Share of Cost as noted in table at right
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | - | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | 4969.0628 | 3138.2687
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | - | -
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 75 | 75 | Utah $50, All others $60 (25% higher)
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 164 | 164 | 2024 Avista Update: $44 + $10/month fee per tstat | Pacificorp assumes 5% of equipment+install costs
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0 | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 0 | 0 | Bring Your Own Thermostat program
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0 | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0 | 0
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 36 | 36 | 2016 M&V Report Event Hours
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0 | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0 | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 20 | 20 | Assume $20 per year per system, same as CAC DLC.
General ServiceProgram Life | Program Life | years | General Service | 10 | 10
General ServiceProgram Start Year | Program Start Year | year | General Service | 2026 | 2026
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1 | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1 | 1
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)

## Ancillary Cooling
| Program Option: | Ancillary Cooling |  | Market PotentialWA | Market PotentialID |  |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes |  | Residential | #REF! | #REF!
|  |  |  | State | State |  |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  |  | Large General Service | #REF! | #REF!
| ParticipationRate | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 10% | 10% | Half of Thermostat Participation given an additional $20 as incentive |  | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 5 | 5 |  |  | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 1% | 1% |  |  | General Service | #REF! | #REF!
[8 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 0% | 0%
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential |  |  |  |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential | 0.25 | 0.25 | Half of parent thermostat impact for ancillary |  | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential |  |  |  |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | 21647.2593 | 12474.6859 | Half for Ancillary- tied to participation reduction from parent program |  |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | - | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | 17317.8074 | 9979.7487 | Half for Ancillary- tied to participation reduction from parent program |  |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 60 | 60 | Utah $50, All others $60 (20% higher) |  |  |  |  | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 0 | 0 | Zero for Ancillary |  |  |  |  | 60000
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | 0 | [5 empty] | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 0 | 0 | BYOT |  |  |  |  | 75000
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | 0 | [6 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | 0 | [5 empty] | Residential | 57.73% | 33.27%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 36 | 36 | 2016 M&V Report Event Hours |  |  |  |  | General Service | 5.521% | 3.487%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | [7 empty] | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential |  | 0 | [5 empty] | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0 | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 20 | 20 | Assume $20 per year per system, same as CAC DLC. Adding $20 to account for ancillary service option |  |  |  |  | Total | 63.25% | 36.75% | 100%
ResidentialProgram Life | Program Life | years | Residential | 10 | 10
ResidentialProgram Start Year | Program Start Year | year | Residential | 2026 | 2026
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1 | 1
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1 | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 10% | 10% | NWPC Smart Thermostat cooling assumption- 5 yr ramp rate- Half for Ancillary
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 5 | 5
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1% | 1%
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 0% | 0%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service |  |  |  |  | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 0.625 | 0.625 | NWPC DLC Switch cooling assumption (East)- Half impact for ancillary | 0.625 | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service |  |  |  |  | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | 2070.4428 | 1307.612 | Half for Ancillary- tied to participation reduction from parent program
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | - | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | 1656.3543 | 1046.0896 | Half for Ancillary- tied to participation reduction from parent program
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | - | -
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 75 | 75 | Utah $50, All others $60 (25% higher)
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 0 | 0 | Zero since part of parent program
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0 | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 0 | 0 | Bring Your Own Thermostat program
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0 | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0 | 0
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 36 | 36 | 2016 M&V Report Event Hours
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0 | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0 | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 20 | 20 | Assume $20 per year per system, same as CAC DLC. Adding $20 to account for ancillary service option
General ServiceProgram Life | Program Life | years | General Service | 10 | 10
General ServiceProgram Start Year | Program Start Year | year | General Service | 2026 | 2026
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1 | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1 | 1
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)

## DLC Smart Thermostats - Heating
| Program Option: | DLC Smart Thermostats - Heating |  | Market PotentialWA | Market PotentialID |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes | Residential | #REF! | #REF!
|  |  |  | State | State |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  | Large General Service | #REF! | #REF!
| ParticipationRate | [5 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 5% | 5% | Assuming maximum participation for combined DLC Cooling and Smart Therm is 25%, reduced from 30% to account for those program participants who may have intended to participate but were unable to correctly install their thermostat | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 5 | 5 |  | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 1% | 1% |  | General Service | #REF! | #REF!
[7 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [5 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 0% | 0%
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential |  |  |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential |  |  |  | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential |  |  |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential | 1.09 | 1.09 | NWPC Smart thermostat heating assumption- general service uses 0.54 (switch to thermostat impact ratio) of eastern switch impact
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential |  |  | Program would piggy-back off of Thermostats-Cooling and share those costs |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | - | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential |  |  | Program would piggy-back off of Thermostats-Cooling and share those costs |  |  |  | Allocation based on share of 2042 (20-year) Winter MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 60 | 60 | Utah $50, All others $60 (20% higher) |  |  |  | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential |  |  | Program would piggy-back off of Thermostats-Cooling and share those costs |  |  |  | 0
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | 0 |  |  |  |  | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 0 | 0 | Bring your own thermostat program |  |  |  | 0
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | 0 | [5 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | 0 |  |  |  |  | Residential | 61.41% | 34.62%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | [6 empty] | General Service | 2.316% | 1.648%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 36 | 36 | 2016 M&V Report Event Hours |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential |  | 0 |  |  |  |  | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0 | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 20 | 20 | Assume $20 per year per system, same as CAC DLC. |  |  |  | Total | 63.73% | 36.27% | 100%
ResidentialProgram Life | Program Life | years | Residential | 10 | 10
ResidentialProgram Start Year | Program Start Year | year | Residential | 2026 | 2026
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1 | 1
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1 | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 3% | 3% | Dropping to 3% to compensate for higher space heating saturations
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 5 | 5
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1% | 1%
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 0% | 0%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service |  |  |  | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service |  |  |  | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service |  |  |  | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service | 1.35 | 1.35 | NWPC Smart thermostat heating assumption- general service uses 0.54 (switch to thermostat impact ratio) of eastern switch impact of 2.5 | 1.35
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service |  |  | Program would piggy-back off of Thermostats-Cooling and share those costs
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | - | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service |  |  | Program would piggy-back off of Thermostats-Cooling and share those costs
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 75 | 75 | Utah $50, All others $60 (25% higher)
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service |  |  | Program would piggy-back off of Thermostats-Cooling and share those costs
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0 | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 0 | 0 | Bring your own thermostat program
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0 | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0 | 0
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | 36 | 36 | 2016 M&V Report Event Hours
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0 | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0 | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 20 | 20 | Assume $20 per year per system, same as CAC DLC.
General ServiceProgram Life | Program Life | years | General Service | 10 | 10
General ServiceProgram Start Year | Program Start Year | year | General Service | 2026 | 2026
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1 | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1 | 1
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)

## Ancillary Heating
| Program Option: | Ancillary Heating |  | Market PotentialWA | Market PotentialID |  |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes |  | Residential | #REF! | #REF!
|  |  |  | State | State |  |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  |  | Large General Service | #REF! | #REF!
| ParticipationRate | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 2.5% | 2.5% | Half for ancillary |  | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 5 | 5 |  |  | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 1% | 1% |  |  | General Service | #REF! | #REF!
[8 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 0% | 0%
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential |  |  |  |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential |  |  |  |  | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential |  |  |  |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential | 0.545 | 0.545 | Half of Smart Thermostat Heating Per-Customer Impact | 0.545
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential |  |  | Program would piggy-back off of Ancillary-Cooling and share those costs |  |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | - | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential |  |  | Program would piggy-back off of Ancillary-Cooling and share those costs |  |  |  |  | Allocation based on share of 2042 (20-year) Winter MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 60 | 60 | Utah $50, All others $60 (20% higher) |  |  |  |  | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 0 | 0 | Zero for Ancillary |  |  |  |  | 0
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | 0 | [5 empty] | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 0 | 0 | Bring your own thermostat program |  |  |  |  | 0
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | 0 | [6 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | 0 | [5 empty] | Residential | 61.41% | 34.62%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | [7 empty] | General Service | 2.316% | 1.648%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 36 | 36 | 2016 M&V Report Event Hours |  |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential |  | 0 | [5 empty] | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0 | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 20 | 20 | Assume $20 per year per system, same as CAC DLC. |  |  |  |  | Total | 63.73% | 36.27% | 100%
ResidentialProgram Life | Program Life | years | Residential | 10 | 10
ResidentialProgram Start Year | Program Start Year | year | Residential | 2026 | 2026
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1 | 1
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1 | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 1.5% | 1.5% | Dropping to 3% to compensate for higher space heating saturations- half for ancillary
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 5 | 5
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1% | 1%
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 0% | 0%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service |  |  |  |  | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service |  |  |  |  | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service |  |  |  |  | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service | 0.675 | 0.675 | Half of parent Smart Thermostat-Heating per-customer impacts | 0.675 | Half for ancillary
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service |  |  | Program would piggy-back off of Ancillary-Cooling and share those costs
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | - | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service |  |  | Program would piggy-back off of Ancillary-Cooling and share those costs
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 75 | 75 | Utah $50, All others $60 (25% higher)
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 0 | 0 | Zero for Ancillary
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0 | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 0 | 0 | Bring your own thermostat program
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0 | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0 | 0
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | 36 | 36 | 2016 M&V Report Event Hours
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0 | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0 | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 20 | 20 | Assume $20 per year per system, same as CAC DLC.
General ServiceProgram Life | Program Life | years | General Service | 10 | 10
General ServiceProgram Start Year | Program Start Year | year | General Service | 2026 | 2026
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1 | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1 | 1
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)

## DLC Water Heating
| Program Option: | DLC Water Heating |  | Market PotentialWA | Market PotentialID |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes | Residential | #REF! | #REF!
|  |  |  | State | State |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  | Large General Service | #REF! | #REF!
| ParticipationRate | [5 empty] | Extra Large General Service | #REF! | #REF! | 25% | PLMA | http://c.ymcdn.com/sites/www.peakload.org/resource/resmgr/PLMA_Water_Heater_Demand_Man.pdf
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential |  | 15% | Ensure population applies to the subset of customers participating in AC or Space Heating DLC- 25% max using studies from PLMA, BGE, and Brattle | ID |  |  | 8.715% | BGE | http://webapp.psc.state.md.us/newIntranet/casenum/NewIndex3_VOpenFile.cfm?ServerFilePath=C:%5CCasenum%5C9100-9199%5C9154%5C%5C719.pdf
ResidentialProgram ramp up period | Program ramp up period | Years | Residential |  | 5 |  | Residential | #REF! | #REF! | 25% | PGE Brattle
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential |  | 1% |  | General Service | #REF! | #REF!
[7 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [5 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential |  | 0%
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential |  |  |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential |  | 0.2 | NWPC Electric Resistance Switch Summer Impact, derated to align with Wh proportion of peak load from EE study | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential |  |  |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential |  | 0.2 | NWPC Electric Resistance Switch Winter Impact, derated to align with Wh proportion of peak load from EE study
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential |  | 67720.0061 |  |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential |  | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential |  | 81264.0073 | Share of Cost as noted in table at right |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential |  | - | [8 empty] | Season | Summer | Summer | Winter | Winter | All
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential |  | 60 | Same as DLC CAC |  |  |  | Table to Allocate Program Admin Cost |  |  |  |  | Old | New Standard Impact | Old | New Standard Impact | Max
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential |  | 23 | Assume 5% of equipment + install costs. |  |  |  | 90000 |  |  |  | DLC WH | 0.5 | 0.2 | 0.5 | 0.2 | 0.23
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential |  | 0 |  |  |  |  | Table to Allocate Program Development Cost |  |  |  | CTA ER | 0.347 | 0.1388 | 0.374 | 0.1496 | 0.23
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential |  | 460 | Assumed $160 cost for water heater switch (same as cooling switch cost), plus $200 installation cost. Cost of Permit and License is $100 for res and $125 for C&I |  |  |  | 75000 |  |  |  | CTA HP | 0.085 | 0.034 | 0.223 | 0.0892 | 0.23
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential |  | 0 | [5 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential |  | 0 |  |  |  |  | Residential | 0% | 90.29%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential |  | 0 | Current PC Cool Keeper CAC DLC program allows for max 100 hours of curtailment. |  |  |  | General Service | 0% | 9.707%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential |  | 50 | Split 50 hrs summer, and 50 hrs winter |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential |  | 0 |  |  |  |  | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential |  | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential |  | 24 | Assume $2/month year round |  |  |  | Total | 0% | 100% | 100%
ResidentialProgram Life | Program Life | years | Residential |  | 8
ResidentialProgram Start Year | Program Start Year | year | Residential |  | 2026 | Existing programs in UT. Other states need 2 years to ramp up.
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential |  | 1
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential |  | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service |  | 5% | * Changed from 3% to reflect a Brattle Study to the left that estimates 5-10% | 5-10% | http://www.brattle.com/system/publications/pdfs/000/004/465/original/Direct_Load_Control_of_Residential_Air_Conditioners_in_Texas_Faruqui_PUCT_Oct_25_2012.pdf?1378772107
General ServiceProgram ramp up period | Program ramp up period | Years | General Service |  | 5 |  | 2% | PGE Brattle
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service |  | 1% | 0
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service |  | 0%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service |  |  |  | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service |  | 0.504 | 7th Plan, pg 25 from Cadmnus Report, Commercial: Res value multiplied by the CAC DLC ratio (small C&I impact /Res impact) | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service |  |  |  | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service |  | 0.504 | 7th Plan, pg 25 from Cadmnus Report, Commercial: Res value multiplied by the CAC DLC ratio (small C&I impact /Res impact)
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service |  | 7279.9939 | No startup costs; Framework already exists for current programs
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service |  | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service |  | 8735.9927 | Share of Cost as noted in table at right
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service |  | -
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service |  | 75 | Same as DLC CAC
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service |  | 24.25 | Assume 5% of equipment + install costs.
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service |  | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service |  | 485 | Assumed $160 cost for water heater switch (same as cooling switch cost), plus $200 installation cost. Cost of Permit and License is $100 for res and $125 for C&I
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service |  | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service |  | 0
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service |  | 0 | Current PC Cool Keeper CAC DLC program allows for max 100 hours of curtailment.
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service |  | 50 | Split 50 hrs summer, and 50 hrs winter
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service |  | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service |  | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service |  | 24 | Assume $2/month year round
General ServiceProgram Life | Program Life | years | General Service |  | 8
General ServiceProgram Start Year | Program Start Year | year | General Service |  | 2026 | Existing programs in UT. Other states need 2 years to ramp up.
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service |  | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service |  | 1
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)
Note on O6: Nielsen, Victoria: Max participation

## Ancillary DLC WH
| Program Option: | Ancillary DLC WH |  | Market PotentialWA | Market PotentialID |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes | Residential | #REF! | #REF!
|  |  |  | State | State |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  | Large General Service | #REF! | #REF!
| ParticipationRate | [5 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential |  | 15% | Ensure population applies to the subset of customers participating in AC or Space Heating DLC | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential |  | 5 |  | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential |  | 1% |  | General Service | #REF! | #REF!
[7 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [5 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential |  | 0%
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential |  |  |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential |  | 0.2 | NWPC Electric Resistance Switch Summer Impact, derated to align with Wh proportion of peak load from EE study | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential |  |  |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential |  | 0.2 | NWPC Electric Resistance Switch Winter Impact, derated to align with Wh proportion of peak load from EE study
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential |  | 67720.0061 |  |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential |  | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential |  | 54176.0049 | Share of Cost as noted in table at right |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential |  | -
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential |  | 60 | Same as DLC CAC |  |  |  | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential |  | 0 | Zero for Ancillary |  |  |  | 60000
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential |  | 0 |  |  |  |  | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential |  | 0 | Zero for Ancillary |  |  |  | 75000
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential |  | 0 | [5 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential |  | 0 |  |  |  |  | Residential | 0% | 90.29%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential |  | 0 | Current PC Cool Keeper CAC DLC program allows for max 100 hours of curtailment. |  |  |  | General Service | 0% | 9.707%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential |  | 50 | Split 50 hrs summer, and 50 hrs winter |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential |  | 0 |  |  |  |  | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential |  | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential |  | 24 | Assume $2/month year round |  |  |  | Total | 0% | 100% | 100%
ResidentialProgram Life | Program Life | years | Residential |  | 8
ResidentialProgram Start Year | Program Start Year | year | Residential |  | 2026 | Existing programs in UT. Other states need 2 years to ramp up.
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential |  | 1
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential |  | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service |  | 5% | * Changed from 3% to reflect a Brattle Study to the left that estimates 5-10%
General ServiceProgram ramp up period | Program ramp up period | Years | General Service |  | 5
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service |  | 1%
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service |  | 0%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service |  |  |  | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service |  | 0.504 | 7th Plan, pg 25 from Cadmnus Report, Commercial: Res value multiplied by the CAC DLC ratio (small C&I impact /Res impact) | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service |  |  |  | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service |  | 0.504 | 7th Plan, pg 25 from Cadmnus Report, Commercial: Res value multiplied by the CAC DLC ratio (small C&I impact /Res impact)
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service |  | 7279.9939 | No startup costs; Framework already exists for current programs
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service |  | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service |  | 5823.9951 | Share of Cost as noted in table at right
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service |  | -
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service |  | 75 | Same as DLC CAC
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service |  | 0 | Zero for Ancillary
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service |  | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service |  | 0 | Zero for Ancillary
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service |  | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service |  | 0
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service |  | 0 | Current PC Cool Keeper CAC DLC program allows for max 100 hours of curtailment.
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service |  | 0 | Split 50 hrs summer, and 50 hrs winter
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service |  | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service |  | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service |  | 24 | Assume $2/month year round
General ServiceProgram Life | Program Life | years | General Service |  | 8
General ServiceProgram Start Year | Program Start Year | year | General Service |  | 2026 | Existing programs in UT. Other states need 2 years to ramp up.
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service |  | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service |  | 1
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)

## Pilot-CTA-2045 HPWH (hidden)
| Program Option: | CTA-2045 HPWH |  | Market PotentialWA | Market PotentialID |  |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes |  | Residential | #REF! | #REF!
|  |  |  | State | State |  |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  |  | Large General Service | #REF! | #REF!
| ParticipationRate | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 1.6% |  | Modified to reflect pilot scope |  | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 3.5 |  |  |  | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 1% |  |  |  | General Service | #REF! | #REF!
[8 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 3% |  | Ability for customers to easily override event- using 3% as placeholder
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential |  |  |  |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential | 0.09 |  | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential |  |  |  |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential | 0.14 |  | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | 7899.694 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | 9479.6328 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential | -
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 60 |  | Same as Smart Thermostats | Higher marketing cost to reach 25% participation |  |  |  | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 0 | [6 empty] | 90000
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | [6 empty] | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 170 |  | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 for these customers)- average customer will be $170 |  |  |  |  | 75000
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | [7 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | [6 empty] | Residential | 21.07% | 0%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 75 |  | 25 total events around 3 hrs ea. |  |  |  |  | General Service | 78.93% | 0%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 75 |  | 25 total events around 3 hrs ea. |  |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential | 0 | [6 empty] | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 24 |  | Assume $2/month year round |  |  |  |  | Total | 100% | 0% | 100%
ResidentialProgram Life | Program Life | years | Residential | 8
ResidentialProgram Start Year | Program Start Year | year | Residential | 2024 | [7 empty] | Updated: | 2022-02-23
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1 |  |  |  |  | BPA 2018 CTA-2045 Water Heater Demonstration Report |  |  |  | EE Potential Assessment purchase share assumptions | EE Study weighted impacts |  |  |  | Peak Mitigation Impacts
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1 |  |  |  |  | Winter AM | Winter PM | Summer AM | Summer PM | <55 gal WHs | Winter AM | Winter PM | Summer AM | Summer PM | Winter AM | Winter PM | Summer AM | Summer PM
[8 empty] | Electric Resistance | 0.562 | 0.563 | 0.393 | 0.389 | 96.85% | 0.55198 | 0.55052 | 0.38446 | 0.37977 | 0.374 | 0.321 | n/a | 0.347
[8 empty] | Heat Pump | 0.244 | 0.167 | 0.122 | 0.096 | 3.151% |  |  |  |  | 0.223 | 0.165 | n/a | 0.085
[9 empty] | BPA 2018 CTA-2045 Water Heater Demonstration Report |  |  | Source: | https://www.bpa.gov/EE/Technology/demand-response/Documents/Demand%20Response%20-%20FINAL%20REPORT%20110918.pdf
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 1.5% |  | Modified to reflect pilot scope
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 3.5
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1%
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 3%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service |  |  |  |  | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 0.225 |  | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service |  |  |  |  | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service | 0.35 |  | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | 29600.306 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | 35520.3672 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | -
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 75 |  | Same as Smart Thermostats
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 0
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 170 |  | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 install cost for these customers)- average customer will be $170
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 75 |  | 25 total events around 3 hrs ea.
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | 75 |  | 25 total events around 3 hrs ea.
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 24 |  | Assume $2/month year round
General ServiceProgram Life | Program Life | years | General Service | 8
General ServiceProgram Start Year | Program Start Year | year | General Service | 2024
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)

## Parent-CTA-2045 HPWH
| Program Option: | CTA-2045 HPWH |  | Market PotentialWA | Market PotentialID |  |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes |  | Residential | #REF! | #REF!
|  |  |  | State | State |  |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  |  | Large General Service | #REF! | #REF!
| ParticipationRate | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 50% |  | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate | Saturation of CTA-2045 water heaters expected to be in 9% of homes by 2026 | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 10 |  |  |  | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 1% |  |  |  | General Service | #REF! | #REF!
[8 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 3% |  | Ability for customers to easily override event- using 3% as placeholder
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential |  |  |  |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential | 0.09 |  | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential |  |  |  |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential | 0.14 |  | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | 7899.694 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | 9479.6328 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential | - | [12 empty] | Season | Summer | Summer | Winter | Winter | All
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 60 |  | Same as Smart Thermostats | Higher marketing cost to reach 25% participation |  |  |  | Table to Allocate Program Admin Cost | [6 empty] | Old | New Standard Impact | Old | New Standard Impact | Max
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 0 | [6 empty] | 90000 | [5 empty] | DLC WH | 0.5 | 0.2 | 0.5 | 0.2 | 0.23
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | [6 empty] | Table to Allocate Program Development Cost | [5 empty] | CTA ER | 0.347 | 0.1388 | 0.374 | 0.1496 | 0.23
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 170 |  | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 for these customers)- average customer will be $170 |  |  |  |  | 75000 | [5 empty] | CTA HP | 0.085 | 0.034 | 0.223 | 0.0892 | 0.23
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | [7 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | [6 empty] | Residential | 21.07% | 0%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 210 |  | 2024 Avista Update: 70 events each season, 3 hours each | 25 total events around 3 hrs ea. |  |  |  | General Service | 78.93% | 0%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 210 |  | 2024 Avista Update: 70 events each season, 3 hours each | 25 total events around 3 hrs ea. |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential | 0 | [6 empty] | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 24 |  | Assume $2/month year round |  |  |  |  | Total | 100% | 0% | 100%
ResidentialProgram Life | Program Life | years | Residential | 8
ResidentialProgram Start Year | Program Start Year | year | Residential | 2026 | [7 empty] | Updated: | 2022-02-23
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1 |  |  |  |  | BPA 2018 CTA-2045 Water Heater Demonstration Report |  |  |  | EE Potential Assessment purchase share assumptions | EE Study weighted impacts |  |  |  | Peak Mitigation Impacts
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1 |  |  |  |  | Winter AM | Winter PM | Summer AM | Summer PM | <55 gal WHs | Winter AM | Winter PM | Summer AM | Summer PM | Winter AM | Winter PM | Summer AM | Summer PM
[8 empty] | Electric Resistance | 0.562 | 0.563 | 0.393 | 0.389 | 96.85% | 0.55198 | 0.55052 | 0.38446 | 0.37977 | 0.374 | 0.321 | n/a | 0.347
[8 empty] | Heat Pump | 0.244 | 0.167 | 0.122 | 0.096 | 3.151% |  |  |  |  | 0.223 | 0.165 | n/a | 0.085
[9 empty] | BPA 2018 CTA-2045 Water Heater Demonstration Report |  |  | Source: | https://www.bpa.gov/EE/Technology/demand-response/Documents/Demand%20Response%20-%20FINAL%20REPORT%20110918.pdf
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 50% |  | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 10
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1%
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 3%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service |  |  |  |  | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 0.225 |  | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service |  |  |  |  | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service | 0.35 |  | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.56x of res
| CEInput | [8 empty] | Grid-interactive Peak Demand from EE study
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | 29600.306 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  |  |  | Winter | Summer
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | - |  |  |  |  | Electric Resistance kW | 0.37 | 0.16
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | 35520.3672 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  |  | Heat Pump kW | 0.14 | 0.09
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | -
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 75 |  | Same as Smart Thermostats
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 0
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 170 |  | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 install cost for these customers)- average customer will be $170
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 210 |  | 2024 Avista Update: 70 events each season, 3 hours each | 25 total events around 3 hrs ea.
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | 210 |  | 2024 Avista Update: 70 events each season, 3 hours each | 25 total events around 3 hrs ea.
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 24 |  | Assume $2/month year round
General ServiceProgram Life | Program Life | years | General Service | 8
General ServiceProgram Start Year | Program Start Year | year | General Service | 2026
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1
Note on O26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Removed Development costs from parent program. Modeling up-front costs in the pilot Reply: For "Considered" program scenario, all costs stay in parents. No pilots.

## Pilot-Ancillary HPWH (hidden)
| Program Option: | Ancillary HPWH |  | Market PotentialWA | Market PotentialID |  |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes |  | Residential | #REF! | #REF!
|  |  |  | State | State |  |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  |  | Large General Service | #REF! | #REF!
| ParticipationRate | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 1.6% |  | Modified to reflect pilot scope |  | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 3.5 |  |  |  | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 1% |  |  |  | General Service | #REF! | #REF!
[8 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 3% |  | Ability for customers to easily override event- using 3% as placeholder
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential |  |  |  |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential | 0.09 |  | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential |  |  |  |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential | 0.14 |  | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | #N/A |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | #N/A |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential | -
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 60 |  | Same as Smart Thermostats | Higher marketing cost to reach 25% participation |  |  |  | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 0 | [6 empty] | 60000
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | [6 empty] | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 0 |  | Zero for Ancillary |  |  |  |  | 75000
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | [7 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | [6 empty] | Residential | #N/A | #N/A
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 75 |  | 25 total events around 3 hrs ea. |  |  |  |  | General Service | #N/A | #N/A
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 75 |  | 25 total events around 3 hrs ea. |  |  |  |  | Large General Service | #N/A | #N/A
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential | 0 | [6 empty] | Extra Large General Service | #N/A | #N/A
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 24 |  | Assume $2/month year round |  |  |  |  | Total | #N/A | #N/A | #N/A
ResidentialProgram Life | Program Life | years | Residential | 8
ResidentialProgram Start Year | Program Start Year | year | Residential | 2024
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 1.5% |  | Modified to reflect pilot scope
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 3.5
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1%
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 3%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service |  |  |  |  | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 0.225 |  | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service |  |  |  |  | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service | 0.35 |  | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | #N/A |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | #N/A |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | -
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 75 |  | Same as Smart Thermostats
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 0
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 0 |  | Zero for Ancillary
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 75 |  | 25 total events around 3 hrs ea.
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | 75 |  | 25 total events around 3 hrs ea.
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 24 |  | Assume $2/month year round
General ServiceProgram Life | Program Life | years | General Service | 8
General ServiceProgram Start Year | Program Start Year | year | General Service | 2024
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)

## Parent-Ancillary HPWH
| Program Option: | Parent-Ancillary HPWH |  | Market PotentialWA | Market PotentialID |  |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes |  | Residential | #REF! | #REF!
|  |  |  | State | State |  |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  |  | Large General Service | #REF! | #REF!
| ParticipationRate | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 50% |  | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate (Half of eligible population) |  | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 10 |  |  |  | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 1% |  |  |  | General Service | #REF! | #REF!
[8 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 3% |  | Ability for customers to easily override event- using 3% as placeholder
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential |  |  |  |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential | 0.09 |  | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study |  | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential |  |  |  |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential | 0.14 |  | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH peak load from EE study
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | 7899.694 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | 6319.7552 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential | -
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 60 |  | Same as Smart Thermostats | Higher marketing cost to reach 25% participation |  |  |  | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 0 | [6 empty] | 60000
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | [6 empty] | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 0 |  | Zero for Ancillary |  |  |  |  | 75000
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | [7 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | [6 empty] | Residential | 21.07% | 0%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 75 |  | 25 total events around 3 hrs ea. |  |  |  |  | General Service | 78.93% | 0%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 75 |  | 25 total events around 3 hrs ea. |  |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential | 0 | [6 empty] | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 24 |  | Assume $2/month year round |  |  |  |  | Total | 100% | 0% | 100%
ResidentialProgram Life | Program Life | years | Residential | 8
ResidentialProgram Start Year | Program Start Year | year | Residential | 2026
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 50% |  | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 10
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1%
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 3%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service |  |  |  |  | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 0.225 |  | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service |  |  |  |  | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service | 0.35 |  | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | 29600.306 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | 23680.2448 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | -
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 75 |  | Same as Smart Thermostats
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 0
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 0 |  | Zero for Ancillary
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 75 |  | 25 total events around 3 hrs ea.
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | 75 |  | 25 total events around 3 hrs ea.
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 24 |  | Assume $2/month year round
General ServiceProgram Life | Program Life | years | General Service | 8
General ServiceProgram Start Year | Program Start Year | year | General Service | 2026
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)
Note on O26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Removed Development costs from parent program. Modeling up-front costs in the pilot Reply: For "Considered" program scenario, all costs stay in parents. No pilots.

## Pilot-CTA-2045 ERWH (hidden)
| Program Option: | CTA-2045 ERWH |  | Market PotentialWA | Market PotentialID |  |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes |  | Residential | #REF! | #REF!
|  |  |  | State | State |  |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  |  | Large General Service | #REF! | #REF!
| ParticipationRate | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 8.8% |  | Modified to reflect pilot scope |  | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 3.5 |  |  |  | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 1% |  |  |  | General Service | #REF! | #REF!
[8 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 3% |  | Ability for customers to easily override event- using 3% as placeholder
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential |  |  |  |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential | 0.16 |  | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH proportion of peak load from EE study |  | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential |  |  |  |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential | 0.37 |  | BPA 2018 CTA-2045 Water Heater Demonstration Report- Winter AM impact, derated to align with WH proportion of peak load from EE study
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | 34070.8725 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | 40885.047 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential | -
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 60 |  | Same as Smart Thermostats | Higher marketing cost to reach 25% participation |  |  |  | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 0 | [6 empty] | 90000
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | [6 empty] | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 170 |  | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 for these customers)- average customer will be $170 |  |  |  |  | 75000
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | [7 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | [6 empty] | Residential | 90.86% | 0%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 75 |  | 25 total events around 3 hrs ea. |  |  |  |  | General Service | 9.144% | 0%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 75 |  | 25 total events around 3 hrs ea. |  |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential | 0 | [6 empty] | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 24 |  | Assume $2/month year round |  |  |  |  | Total | 100% | 0% | 100%
ResidentialProgram Life | Program Life | years | Residential | 8
ResidentialProgram Start Year | Program Start Year | year | Residential | 2024 | [7 empty] | Updated: | 2022-02-23
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1 |  |  |  |  | BPA 2018 CTA-2045 Water Heater Demonstration Report |  |  |  | EE Potential Assessment purchase share assumptions | EE Study weighted impacts |  |  |  | Peak Mitigation Impacts
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1 |  |  |  |  | Winter AM | Winter PM | Summer AM | Summer PM | <55 gal WHs | Winter AM | Winter PM | Summer AM | Summer PM | Winter AM | Winter PM | Summer AM | Summer PM
[8 empty] | Electric Resistance | 0.562 | 0.563 | 0.393 | 0.389 | 96.85% | 0.55198 | 0.55052 | 0.38446 | 0.37977 | 0.374 | 0.321 | n/a | 0.347
[8 empty] | Heat Pump | 0.244 | 0.167 | 0.122 | 0.096 | 3.151% |  |  |  |  | 0.223 | 0.165 | n/a | 0.085
[9 empty] | BPA 2018 CTA-2045 Water Heater Demonstration Report |  |  | Source: | https://www.bpa.gov/EE/Technology/demand-response/Documents/Demand%20Response%20-%20FINAL%20REPORT%20110918.pdf
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 5% |  | Modified to reflect pilot scope
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 3.5
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1%
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 3%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service |  |  |  |  | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 0.4 |  | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service |  |  |  |  | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service | 0.925 |  | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | 3429.1275 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | 4114.953 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | -
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 75 |  | Same as Smart Thermostats
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 0
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 170 |  | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 install cost for these customers)- average customer will be $170
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 75 |  | 25 total events around 3 hrs ea.
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | 75 |  | 25 total events around 3 hrs ea.
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 24 |  | Assume $2/month year round
General ServiceProgram Life | Program Life | years | General Service | 8
General ServiceProgram Start Year | Program Start Year | year | General Service | 2024
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)

## Parent-CTA-2045 ERWH
| Program Option: | CTA-2045 ERWH |  | Market PotentialWA | Market PotentialID |  |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes |  | Residential | #REF! | #REF!
|  |  |  | State | State |  |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  |  | Large General Service | #REF! | #REF!
| ParticipationRate | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 50% |  | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate | Saturation of CTA-2045 water heaters expected to be in 9% of homes by 2026 | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 11 |  | modified 10-year ramp to reflect transition from pilot |  | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 1% |  |  |  | General Service | #REF! | #REF!
[8 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 3% |  | Ability for customers to easily override event- using 3% as placeholder
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential |  |  |  |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential | 0.16 |  | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH proportion of peak load from EE study |  | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential |  |  |  |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential | 0.37 |  | BPA 2018 CTA-2045 Water Heater Demonstration Report- Winter AM impact, derated to align with WH proportion of peak load from EE study
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | 34070.8725 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | 40885.047 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential | - | [12 empty] | Season | Summer | Summer | Winter | Winter | All
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 60 |  | Same as Smart Thermostats | Higher marketing cost to reach 25% participation |  |  |  | Table to Allocate Program Admin Cost | [6 empty] | Old | New Standard Impact | Old | New Standard Impact | Max
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 0 | [6 empty] | 90000 | [5 empty] | DLC WH | 0.5 | 0.2 | 0.5 | 0.2 | 0.23
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | [6 empty] | Table to Allocate Program Development Cost | [5 empty] | CTA ER | 0.347 | 0.1388 | 0.374 | 0.1496 | 0.23
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 170 |  | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 for these customers)- average customer will be $170 |  |  |  |  | 75000 | [5 empty] | CTA HP | 0.085 | 0.034 | 0.223 | 0.0892 | 0.23
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | [7 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | [6 empty] | Residential | 90.86% | 0%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 75 |  | 25 total events around 3 hrs ea. |  |  |  |  | General Service | 9.144% | 0%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 75 |  | 25 total events around 3 hrs ea. |  |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential | 0 | [6 empty] | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 24 |  | Assume $2/month year round |  |  |  |  | Total | 100% | 0% | 100%
ResidentialProgram Life | Program Life | years | Residential | 8
ResidentialProgram Start Year | Program Start Year | year | Residential | 2026 | [7 empty] | Updated: | 2022-02-23
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1 |  |  |  |  | BPA 2018 CTA-2045 Water Heater Demonstration Report |  |  |  | EE Potential Assessment purchase share assumptions | EE Study weighted impacts |  |  |  | Peak Mitigation Impacts
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1 |  |  |  |  | Winter AM | Winter PM | Summer AM | Summer PM | <55 gal WHs | Winter AM | Winter PM | Summer AM | Summer PM | Winter AM | Winter PM | Summer AM | Summer PM
[8 empty] | Electric Resistance | 0.562 | 0.563 | 0.393 | 0.389 | 96.85% | 0.55198 | 0.55052 | 0.38446 | 0.37977 | 0.374 | 0.321 | n/a | 0.347
[8 empty] | Heat Pump | 0.244 | 0.167 | 0.122 | 0.096 | 3.151% |  |  |  |  | 0.223 | 0.165 | n/a | 0.085
[9 empty] | BPA 2018 CTA-2045 Water Heater Demonstration Report |  |  | Source: | https://www.bpa.gov/EE/Technology/demand-response/Documents/Demand%20Response%20-%20FINAL%20REPORT%20110918.pdf
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 50% |  | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 10
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1%
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 3%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service |  |  |  |  | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 0.4 |  | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service |  |  |  |  | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service | 0.925 |  | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | 3429.1275 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | 4114.953 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | -
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 75 |  | Same as Smart Thermostats
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 0
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 170 |  | $150 for module and comms, 20% of customers will need help provisioning these (an additional $100 install cost for these customers)- average customer will be $170
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 75 |  | 25 total events around 3 hrs ea.
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | 75 |  | 25 total events around 3 hrs ea.
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 24 |  | Assume $2/month year round
General ServiceProgram Life | Program Life | years | General Service | 8
General ServiceProgram Start Year | Program Start Year | year | General Service | 2026
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)
Note on O26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Removed Development costs from parent program. Modeling up-front costs in the pilot Reply: For "Considered" program scenario, all costs stay in parents. No pilots.

## Pilot-Ancillary ERWH (hidden)
| Program Option: | Ancillary ERWH |  | Market PotentialWA | Market PotentialID |  |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes |  | Residential | #REF! | #REF!
|  |  |  | State | State |  |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  |  | Large General Service | #REF! | #REF!
| ParticipationRate | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 8.8% |  | Modified to reflect pilot scope |  | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 3.5 |  |  |  | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 1% |  |  |  | General Service | #REF! | #REF!
[8 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 3% |  | Ability for customers to easily override event- using 3% as placeholder
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential |  |  |  |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential | 0.16 |  | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH proportion of peak load from EE study | Full Impact | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential |  |  |  |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential | 0.37 |  | BPA 2018 CTA-2045 Water Heater Demonstration Report- Winter AM impact, derated to align with WH proportion of peak load from EE study | Full Impact
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | #N/A |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | #N/A |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential | -
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 60 |  | Same as Smart Thermostats | Higher marketing cost to reach 25% participation |  |  |  | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 0 | [6 empty] | 60000
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | [6 empty] | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 0 |  | Zero for Ancillary |  |  |  |  | 75000
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | [7 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | [6 empty] | Residential | #N/A | #N/A
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 75 |  | 25 total events around 3 hrs ea. |  |  |  |  | General Service | #N/A | #N/A
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 75 |  | 25 total events around 3 hrs ea. |  |  |  |  | Large General Service | #N/A | #N/A
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential | 0 | [6 empty] | Extra Large General Service | #N/A | #N/A
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 24 |  | Assume $2/month year round |  |  |  |  | Total | #N/A | #N/A | #N/A
ResidentialProgram Life | Program Life | years | Residential | 8
ResidentialProgram Start Year | Program Start Year | year | Residential | 2024
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 5% |  | Modified to reflect pilot scope
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 3.5
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1%
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 3%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service |  |  |  |  | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 0.4 |  | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service |  |  |  |  | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service | 0.925 |  | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | #N/A |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | #N/A |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | -
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 75 |  | Same as Smart Thermostats
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 0
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 0 |  | Zero for Ancillary
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 75 |  | 25 total events around 3 hrs ea.
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | 75 |  | 25 total events around 3 hrs ea.
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 24 |  | Assume $2/month year round
General ServiceProgram Life | Program Life | years | General Service | 8
General ServiceProgram Start Year | Program Start Year | year | General Service | 2024
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)

## Parent-Ancillary ERWH
| Program Option: | Parent-Ancillary ERWH |  | Market PotentialWA | Market PotentialID |  |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes |  | Residential | #REF! | #REF!
|  |  |  | State | State |  |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  |  | Large General Service | #REF! | #REF!
| ParticipationRate | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 50% |  | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate (Half of eligible population) |  | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 11 |  | modified 10-year ramp to reflect transition from pilot |  | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 1% |  |  |  | General Service | #REF! | #REF!
[8 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 3% |  | Ability for customers to easily override event- using 3% as placeholder
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential |  |  |  |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential | 0.16 |  | BPA 2018 CTA-2045 Water Heater Demonstration Report- Summer PM impact, derated to align with WH proportion of peak load from EE study | Full Impact | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential |  |  |  |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential | 0.37 |  | BPA 2018 CTA-2045 Water Heater Demonstration Report- Winter AM impact, derated to align with WH proportion of peak load from EE study | Full Impact
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | 34070.8725 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | 27256.698 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs |  |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential | -
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 60 |  | Same as Smart Thermostats | Higher marketing cost to reach 25% participation |  |  |  | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 0 | [6 empty] | 60000
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | [6 empty] | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 0 |  | Zero for Ancillary |  |  |  |  | 75000
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | [7 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | [6 empty] | Residential | 90.86% | 0%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 75 |  | 25 total events around 3 hrs ea. |  |  |  |  | General Service | 9.144% | 0%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 75 |  | 25 total events around 3 hrs ea. |  |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential | 0 | [6 empty] | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 24 |  | Assume $2/month year round |  |  |  |  | Total | 100% | 0% | 100%
ResidentialProgram Life | Program Life | years | Residential | 8
ResidentialProgram Start Year | Program Start Year | year | Residential | 2026
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 50% |  | NWPC Electric Resistance Grid-Ready Summer/Winter Participation- 10 yr ramp rate
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 10
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1%
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 3%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service |  |  |  |  | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 0.4 |  | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res |  | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service |  |  |  |  | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service | 0.925 |  | NWPC Electric Resistance Grid-Ready Summer/Winter Impact- General service used 2.5x of res
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | 3429.1275 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | 2743.302 |  | Share of Cost as noted in table at right, Costs shared 50/50 between CTA-2045 programs
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | -
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 75 |  | Same as Smart Thermostats
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 0
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 0 |  | Zero for Ancillary
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 75 |  | 25 total events around 3 hrs ea.
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | 75 |  | 25 total events around 3 hrs ea.
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 24 |  | Assume $2/month year round
General ServiceProgram Life | Program Life | years | General Service | 8
General ServiceProgram Start Year | Program Start Year | year | General Service | 2026
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)
Note on O26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Removed Development costs from parent program. Modeling up-front costs in the pilot Reply: For "Considered" program scenario, all costs stay in parents. No pilots.

## DLC Smart Appliances
| Program Option: | DLC Smart Appliances |  | Market PotentialWA | Market PotentialID |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes | Residential | #REF! | #REF!
|  |  |  | State | State |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  | Large General Service | #REF! | #REF!
| ParticipationRate | [5 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 5% | 5% | 2015 ISACA IT Risk Reward Barometer - US Consumer Results. October 2015. http://www.isaca.org/SiteCollectionDocuments/2015-risk-reward-survey/2015-isaca-risk-reward-consumer-summary-us_res_eng_1015.pdf | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 5 | 5 |  | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 1% | 1% |  | General Service | #REF! | #REF!
[7 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [5 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 0% | 0%
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential |  |  |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential | 0.14 | 0.14 | Ghatikar, Rish. Demand Response Automation in Appliance and Equipment. Lawrence Berkley National Laboratory, 2015. Web. http://docketpublic.energy.ca.gov/PublicDocuments/15-IEPR-05/TN205072_20150618T110004_Demand_Response_Automation_in_Appliances_and_Equipment.pptx kw @ meter values= 0.14 for summer and winter | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential |  |  |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential | 0.14 | 0.14 | Ghatikar, Rish. Demand Response Automation in Appliance and Equipment. Lawrence Berkley National Laboratory, 2015. Web. http://docketpublic.energy.ca.gov/PublicDocuments/15-IEPR-05/TN205072_20150618T110004_Demand_Response_Automation_in_Appliances_and_Equipment.pptx kw @ meter values= 0.14 for summer and winter
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | 43574.695 | 23754.2683 | Share of Cost as noted in table at right |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | - | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | 52289.634 | 28505.1219 | Share of Cost as noted in table at right |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential | - | -
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 50 | 50 |  |  |  |  | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | [6 empty] | 90000
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | 0 |  |  |  |  | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 300 | 300 | Google research revealed devices range anywhere between $150 -400. Need wifi hub or some sort to connect devices. See email between Dave & Victoria 5-9-16 |  |  |  | 75000
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | 0 | [5 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | 0 |  |  |  |  | Residential | 58.1% | 31.67%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 528 | 528 | Pacificorp: Six hours on-peak period each summer weekday |  |  |  | General Service | 5.851% | 4.377%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 528 | 528 | Pacificorp: Six hours on-peak period each winter weekday |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential | 0 | 0 |  |  |  |  | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0 | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 0 | 0 |  |  |  |  | Total | 63.95% | 36.05% | 100%
ResidentialProgram Life | Program Life | years | Residential | 8 | 8
ResidentialProgram Start Year | Program Start Year | year | Residential | 2026 | 2026
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1 | 1
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1 | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 5% | 5% | 2015 ISACA IT Risk Reward Barometer - US Consumer Results. October 2015. http://www.isaca.org/SiteCollectionDocuments/2015-risk-reward-survey/2015-isaca-risk-reward-consumer-summary-us_res_eng_1015.pdf
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 5 | 5
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1% | 1%
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 0% | 0%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 0.14 | 0.14 | Ghatikar, Rish. Demand Response Automation in Appliance and Equipment. Lawrence Berkley National Laboratory, 2015. Web. http://docketpublic.energy.ca.gov/PublicDocuments/15-IEPR-05/TN205072_20150618T110004_Demand_Response_Automation_in_Appliances_and_Equipment.pptx kw @ meter values= 0.14 for summer and winter
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service | 0.14 | 0.14 | Ghatikar, Rish. Demand Response Automation in Appliance and Equipment. Lawrence Berkley National Laboratory, 2015. Web. http://docketpublic.energy.ca.gov/PublicDocuments/15-IEPR-05/TN205072_20150618T110004_Demand_Response_Automation_in_Appliances_and_Equipment.pptx kw @ meter values= 0.14 for summer and winter
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | 4388.6072 | 3282.4296 | Share of Cost as noted in table at right
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | - | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | 5266.3286 | 3938.9155 | Share of Cost as noted in table at right
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | - | -
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 50 | 50
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 0 | 0
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0 | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 300 | 300 | Google research revealed devices range anywhere between $150 -400. Need wifi hub or some sort to connect devices. See email between Dave & Victoria 5-9-16
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0 | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0 | 0
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 528 | 528 | Pacificorp: Six hours on-peak period each summer weekday
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | 528 | 528 | Pacificorp: Six hours on-peak period each winter weekday
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0 | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0 | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 0 | 0
General ServiceProgram Life | Program Life | years | General Service | 8 | 8
General ServiceProgram Start Year | Program Start Year | year | General Service | 2026 | 2026
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1 | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1 | 1

## DLC Electric Vehicle Charging
| Program Option: | DLC Electric Vehicle Charging |  | Market PotentialWA | Market PotentialID |  | Base Year Peak Usage per Customer (kW)
|  | *This is the V1G Telematics Program |  | Market Potential | Market Potential |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes | Res-EV | 0.72264 | 0.72264
|  |  |  | State | State |  | GS-EV | 0.72264 | 0.72264
|  |  |  | WA | ID |  | LGS-EV | 6.6667 | 6.6667
| ParticipationRate | [5 empty] | ELGS-EV | 6.6667 | 6.6667
Res-EVSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Res-EV | 20% |  | WA: 2024 Avista Update; Lowered from 1/3 of EV TOU rate (17%) to 15% based on Avista feedback | ID
Res-EVProgram ramp up period | Program ramp up period | Years | Res-EV | 5 |  |  | Res-EV | 0.72264 | 0.72264
Res-EVProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Res-EV | 1% |  |  | GS-EV | 0.72264 | 0.72264
[7 empty] | LGS-EV | 6.6667 | 6.6667
| ImpactInput | [5 empty] | ELGS-EV | 6.6667 | 6.6667
Res-EVEvent Non-Performance Rate | Event Non-Performance Rate | % | Res-EV | 0%
Res-EVPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Res-EV | 90% |  | 2024 Avista Update | QC- impacts/customer | WA | ID
Res-EVPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Res-EV | 0 |  | Update: Avista 2019 EVSE report claims 75% charging load reduction. Impact based on Res-EV impact/customer. OLD: Based on Avista research, expecting a 90% + Load Shift (0.5 kW) | Summer | 0.65037 | 0
Res-EVPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Res-EV | 90% |  | 2024 Avista Update | Winter | 0.65037 | 0
Res-EVPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Res-EV | 0 |  | Update: Avista 2019 EVSE report claims 75% charging load reduction. Impact based on Res-EV impact/customer. OLD: Based on Avista research, expecting a 90% + Load Shift (0.5 kW)
CEInput
Res-EVProgram Development Cost | Program Development Cost | $/program | Res-EV | 200000 |  | Share of Cost as noted in table at right |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
Res-EVProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Res-EV | 0
Res-EVAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Res-EV | 80000 |  | 2024 Avista Update: Share of Cost as noted in table at right |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
Res-EVAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Res-EV | -
Res-EVPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Res-EV | 350 |  | 2024 Avista Update |  |  |  | Table to Allocate Program Admin Cost
Res-EVAnnual O&M Cost | Annual O&M Cost | $/participant/year | Res-EV | 45 |  | 2024 Avista Update: $45 per car (300 cars minimum) |  |  |  | 80000 | 2024 Avista Update: cell O24 included $20k RER License fee for the entire program
Res-EVAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Res-EV | 0 | [5 empty] | Table to Allocate Program Development Cost
Res-EVCost of Equip + Install | Cost of Equip + Install | $/tech | Res-EV | 500 |  | 10/26: $1766 from Avista 2019 EVSE report. Instead of covering cost fo equipment, Avista wants to model offering a partial incentive. Benchmarked $500 based on WA rebates. OLD: Updated cost of equipment and install to $700 per Avista email on 8/25/2020 |  |  |  | 200000
Res-EVCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Res-EV | 0 | [6 empty] | WA | ID
Res-EVAMI Cost | AMI Cost | $/program/year | Res-EV | 0 | [5 empty] | Res-EV | 100% | 0%
Res-EVSummer DR Event Hours | Summer DR Event Hours | hours/year | Res-EV | 528 |  | Pacificorp: Six hours on-peak period each summer weekday |  |  |  | GS-EV | 0% | 0%
Res-EVWinter DR Event Hours | Winter DR Event Hours | hours/year | Res-EV | 528 |  | Pacificorp: Six hours on-peak period each winter weekday |  |  |  | LGS-EV | 0% | 0%
Res-EVPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Res-EV | 0 | [5 empty] | ELGS-EV | 0% | 0%
Res-EVPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Res-EV | 0
Res-EVPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Res-EV | 60 |  | 2024 Avista Update: $5/month for 1st year; $0 if cust charges 3+ times on peak |  |  |  | Total | 100% | 0% | 100%
Res-EVProgram Life | Program Life | years | Res-EV | 8
Res-EVProgram Start Year | Program Start Year | year | Res-EV | 2025 |  | 2024 Avista Update |  |  |  | State | Class | Peak Load
Res-EVDe-rate | De-rate | capacity equivalence factor | Res-EV | 1 | [5 empty] | WA | Res-EV | 1.2109 | 2024 Avista Update: removed all GS and ID
Res-EVNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Res-EV | 1 | [5 empty] | ID | Res-EV | 0
[10 empty] | WA | GS-EV | 0
[10 empty] | ID | GS-EV | 0
[10 empty] | WA | LGS-EV
[10 empty] | ID | LGS-EV
[10 empty] | WA | ELGS-EV
[10 empty] | ID | ELGS-EV
DTE rate differential
[10 empty] | On-peak | 0.18
[10 empty] | Off-Peak | 0.07 | 2.5714
[11 empty] | Impact | 7%
Avista EVSE Final Report, October 2019

## Ancillary EV
| Program Option: | Ancillary EV |  | Market PotentialWA | Market PotentialID |  |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes |  | Res-EV | 0.72264 | 0.72264
|  |  |  | State | State |  |  | GS-EV | 0.72264 | 0.72264
|  |  |  | WA | ID |  |  | LGS-EV | 6.6667 | 6.6667
| ParticipationRate | [6 empty] | ELGS-EV | 6.6667 | 6.6667
Res-EVSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Res-EV | 15% | 15% | Assumption: One Third of TOU Demand Rate w EV. This participation rate will be throttled / scaled using the equipment saturation for EVs, which will be quite low. |  | ID
Res-EVProgram ramp up period | Program ramp up period | Years | Res-EV | 5 | 5 |  |  | Res-EV | 0.72264 | 0.72264
Res-EVProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Res-EV | 1% | 1% |  |  | GS-EV | 0.72264 | 0.72264
[8 empty] | LGS-EV | 6.6667 | 6.6667
| ImpactInput | [6 empty] | ELGS-EV | 6.6667 | 6.6667
Res-EVEvent Non-Performance Rate | Event Non-Performance Rate | % | Res-EV | 0% | 0%
Res-EVPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Res-EV |  |  |  |  | QC- impacts/customer | WA | ID
Res-EVPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Res-EV | 0.25 | 0.25 | Half of parent impact for ancillary |  | Summer | 34.6% | 34.6%
Res-EVPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Res-EV |  |  |  |  | Winter | 34.6% | 34.6%
Res-EVPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Res-EV | 0.25 | 0.25 | Half of parent impact for ancillary
CEInput
Res-EVProgram Development Cost | Program Development Cost | $/program | Res-EV | 32233.6232 | 16516.3768 | Share of Cost as noted in table at right |  |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
Res-EVProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Res-EV | - | -
Res-EVAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Res-EV | 25786.8986 | 13213.1014 | Share of Cost as noted in table at right |  |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
Res-EVAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Res-EV | - | -
Res-EVPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Res-EV | 50 | 50 | Assumption $50 for RAP C&I, MAP = RAPx1.2 |  |  |  |  | Table to Allocate Program Admin Cost
Res-EVAnnual O&M Cost | Annual O&M Cost | $/participant/year | Res-EV | 0 | 0 | Zero for Ancillary |  |  |  |  | 60000
Res-EVAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Res-EV | 0 | 0 | [5 empty] | Table to Allocate Program Development Cost
Res-EVCost of Equip + Install | Cost of Equip + Install | $/tech | Res-EV | 0 | 0 | Zero for Ancillary |  |  |  |  | 75000
Res-EVCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Res-EV | 0 | 0 | [6 empty] | WA | ID
Res-EVAMI Cost | AMI Cost | $/program/year | Res-EV | 0 | 0 | [5 empty] | Res-EV | 42.98% | 22.02%
Res-EVSummer DR Event Hours | Summer DR Event Hours | hours/year | Res-EV | 528 | 528 | Pacificorp: Six hours on-peak period each summer weekday |  |  |  |  | GS-EV | 20.33% | 14.67%
Res-EVWinter DR Event Hours | Winter DR Event Hours | hours/year | Res-EV | 528 | 528 | Pacificorp: Six hours on-peak period each winter weekday |  |  |  |  | LGS-EV | 0% | 0%
Res-EVPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Res-EV | 0 | 0 | [5 empty] | ELGS-EV | 0% | 0%
Res-EVPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Res-EV | 0 | 0
Res-EVPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Res-EV | 0 | 0 | Avista would provide a rate based charger or give a rebate on it, with no further incentives |  |  |  |  | Total | 63.31% | 36.69% | 100%
Res-EVProgram Life | Program Life | years | Res-EV | 8 | 8
Res-EVProgram Start Year | Program Start Year | year | Res-EV | 2025 | 2025 | 2024 Avista Update | Technology won’t be available for mass market till 2024 |  |  |  | State | Class | Peak Load
Res-EVDe-rate | De-rate | capacity equivalence factor | Res-EV | 1 | 1 | [5 empty] | WA | Res-EV | 1.2109
Res-EVNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Res-EV | 1 | 1 | [5 empty] | ID | Res-EV | 0.62048
[11 empty] | WA | GS-EV | 0.57295
[11 empty] | ID | GS-EV | 0.4132
[11 empty] | WA | LGS-EV
[11 empty] | ID | LGS-EV
[11 empty] | WA | ELGS-EV
| Data Element | Unit | Customer Class | Market Potential | Market Potential | [5 empty] | ID | ELGS-EV
|  |  |  | State | State
|  |  |  | WA | ID | [6 empty] | DTE rate differential
| ParticipationRate | [9 empty] | On-peak | 0.18
GS-EVSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | GS-EV | 15% | 15% | Prelim Assumption: One Third of EV TOU Demand Rate |  |  |  |  | Off-Peak | 0.07 | 2.5714
GS-EVProgram ramp up period | Program ramp up period | Years | GS-EV | 5 | 5 | [6 empty] | Impact | 7%
GS-EVProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | GS-EV | 1% | 1%
ImpactInput
GS-EVEvent Non-Performance Rate | Event Non-Performance Rate | % | GS-EV | 0% | 0%
GS-EVPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | GS-EV | 75% | 75% |  |  | QC- impacts/customer | WA | ID
GS-EVPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | GS-EV | 0 | 0 | Update: Avista 2019 EVSE report claims 75% charging load reduction. Impact based on Res-EV impact/customer. OLD: Based on Avista research, expecting a 90% + Load Shift (0.5 kW) |  | Summer | 0.54198 | 0.54198
GS-EVPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | GS-EV | 75% | 75% |  |  | Winter | 0.54198 | 0.54198
GS-EVPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | GS-EV | 0 | 0 | Update: Avista 2019 EVSE report claims 75% charging load reduction. Impact based on Res-EV impact/customer. OLD: Based on Avista research, expecting a 90% + Load Shift (0.5 kW)
CEInput
GS-EVProgram Development Cost | Program Development Cost | $/program | GS-EV | 15251.1961 | 10998.8039 | Share of Cost as noted in table at right
GS-EVProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | GS-EV | - | -
GS-EVAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | GS-EV | 12200.9568 | 8799.0432 | Share of Cost as noted in table at right
GS-EVAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | GS-EV | - | -
GS-EVPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | GS-EV | 62.5 | 62.5 | 25% higher than residential
GS-EVAnnual O&M Cost | Annual O&M Cost | $/participant/year | GS-EV | 0 | 0 | Zero for Ancillary
GS-EVAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | GS-EV | 0 | 0
GS-EVCost of Equip + Install | Cost of Equip + Install | $/tech | GS-EV | 0 | 0 | Zero for Ancillary
GS-EVCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | GS-EV | 0 | 0
GS-EVAMI Cost | AMI Cost | $/program/year | GS-EV | 0 | 0
GS-EVSummer DR Event Hours | Summer DR Event Hours | hours/year | GS-EV | 528 | 528 | Pacificorp: Six hours on-peak period each summer weekday
GS-EVWinter DR Event Hours | Winter DR Event Hours | hours/year | GS-EV | 528 | 528 | Pacificorp: Six hours on-peak period each winter weekday
GS-EVPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | GS-EV | 0 | 0
GS-EVPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | GS-EV | 0 | 0
GS-EVPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | GS-EV | 0 | 0 | Avista would provide a rate based charger or give a rebate on it, with no further incentives
GS-EVProgram Life | Program Life | years | GS-EV | 8 | 8
GS-EVProgram Start Year | Program Start Year | year | GS-EV | 2025 | 2025 | 2024 Avista Update | Technology won’t be available for mass market till 2024
GS-EVDe-rate | De-rate | capacity equivalence factor | GS-EV | 1 | 1
GS-EVNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | GS-EV | 1 | 1

## Third Party Contracts
| Program Option: | Third Party Contracts |  | Market PotentialWA | Market PotentialID |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes | Residential | #REF! | #REF!
|  |  |  | State | State |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  | Large General Service | #REF! | #REF!
| ParticipationRate | [5 empty] | Extra Large General Service | #REF! | #REF!
Large General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Large General Service | 15% | 15% | 2024 Avista Update | ID
Large General ServiceProgram ramp up period | Program ramp up period | Years | Large General Service | 3 | 3 |  | Residential | #REF! | #REF!
Large General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Large General Service | 1% | 1% |  | General Service | #REF! | #REF!
[7 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [5 empty] | Extra Large General Service | #REF! | #REF!
Large General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | Large General Service | 0% | 0%
Large General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Large General Service | 21% | 21% | weighted average from impacts in the following report: Impact Estimates from Aggregator Programs in California (Source: 2012 Statewide Load Impact Evaluation of California Aggregator Demand Response Programs Volume 1: Ex post and Ex ante Load Impacts; Christensen Associates Energy Consulting; April 1, 2013). | QC- impacts/customer | WA | ID
Large General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Large General Service | 0 | 0 |  | Summer | #REF! | #REF!
Large General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Large General Service | 21% | 21% | weighted average from impacts in the following report: Impact Estimates from Aggregator Programs in California (Source: 2012 Statewide Load Impact Evaluation of California Aggregator Demand Response Programs Volume 1: Ex post and Ex ante Load Impacts; Christensen Associates Energy Consulting; April 1, 2013). | Winter | #REF! | #REF!
Large General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Large General Service | 0 | 0
CEInput
Large General ServiceProgram Development Cost | Program Development Cost | $/program | Large General Service | 0 | 0 | No startup costs; Would be included in 3rd Party Costs |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
Large General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Large General Service | 0 | 0
Large General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Large General Service | 0 | 0 |  |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
Large General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Large General Service | 0 | 0 | Assume 3rd-party program delivery cost of $80/kW (60-80$/kW range). Additional 1% cost for utility overhead/admin costs.
Large General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost |  |  |  | Table to Allocate Program Admin Cost
Large General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost |  |  |  | 150000
Large General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Large General Service | 80000 | 80000 | included in 3rd Party Program Admin Cost |  |  |  | Table to Allocate Program Development Cost
Large General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost |  |  |  | 75000
Large General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost |  |  |  |  | WA | ID
Large General ServiceAMI Cost | AMI Cost | $/program/year | Large General Service | 0 | 0 |  |  |  |  | Residential | 0% | 0%
Large General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | Large General Service | 30 | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  |  |  | General Service | 9.013% | 4.221%
Large General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | Large General Service | 30 | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  |  |  | Large General Service | 45.94% | 18.23%
Large General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost. Capacity reserve incentive pmt given to customers typically in range of $10 to $70 per kW-year |  |  |  | Extra Large General Service | 13.72% | 8.874%
Large General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost. Capacity reserve incentive pmt given to customers typically in range of $10 to $70 per kW-year
Large General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Large General Service | 0 | 0 |  |  |  |  | Total | 68.67% | 31.33% | 100%
Large General ServiceProgram Life | Program Life | years | Large General Service | 3 | 3
Large General ServiceProgram Start Year | Program Start Year | year | Large General Service | 2026 | 2028
Large General ServiceDe-rate | De-rate | capacity equivalence factor | Large General Service | 1 | 1
Large General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Large General Service | 1 | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
Extra Large General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Extra Large General Service | 15% | 15% | 2024 Avista Update
Extra Large General ServiceProgram ramp up period | Program ramp up period | Years | Extra Large General Service | 3 | 3
Extra Large General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Extra Large General Service | 1% | 1%
ImpactInput
Extra Large General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | Extra Large General Service | 0% | 0%
Extra Large General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Extra Large General Service | 21% | 21% | weighted average from impacts in the following report: Impact Estimates from Aggregator Programs in California (Source: 2012 Statewide Load Impact Evaluation of California Aggregator Demand Response Programs Volume 1: Ex post and Ex ante Load Impacts; Christensen Associates Energy Consulting; April 1, 2013). | QC- impacts/customer | WA | ID
Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Extra Large General Service | 0 | 0 |  | Summer | #REF! | #REF!
Extra Large General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Extra Large General Service | 21% | 21% | weighted average from impacts in the following report: Impact Estimates from Aggregator Programs in California (Source: 2012 Statewide Load Impact Evaluation of California Aggregator Demand Response Programs Volume 1: Ex post and Ex ante Load Impacts; Christensen Associates Energy Consulting; April 1, 2013). | Winter | #REF! | #REF!
Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Extra Large General Service | 0 | 0
CEInput
Extra Large General ServiceProgram Development Cost | Program Development Cost | $/program | Extra Large General Service | 0 | 0 | No startup costs; Would be included in 3rd Party Costs
Extra Large General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Extra Large General Service | 0 | 0
Extra Large General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Extra Large General Service | 0 | 0
Extra Large General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Extra Large General Service | 0 | 0 | Assume 3rd-party program delivery cost of $80/kW (60-80$/kW range). Additional 1% cost for utility overhead/admin costs.
Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Extra Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost
Extra Large General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | Extra Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost
Extra Large General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Extra Large General Service | 80000 | 80000 | included in 3rd Party Program Admin Cost
Extra Large General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | Extra Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost
Extra Large General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Extra Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost
Extra Large General ServiceAMI Cost | AMI Cost | $/program/year | Extra Large General Service | 0 | 0
Extra Large General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | Extra Large General Service | 30 | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event.
Extra Large General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | Extra Large General Service | 30 | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event.
Extra Large General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Extra Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost. Capacity reserve incentive pmt given to customers typically in range of $10 to $70 per kW-year
Extra Large General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Extra Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost. Capacity reserve incentive pmt given to customers typically in range of $10 to $70 per kW-year
Extra Large General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Extra Large General Service | 0 | 0
Extra Large General ServiceProgram Life | Program Life | years | Extra Large General Service | 3 | 3
Extra Large General ServiceProgram Start Year | Program Start Year | year | Extra Large General Service | 2026 | 2028
Extra Large General ServiceDe-rate | De-rate | capacity equivalence factor | Extra Large General Service | 1 | 1
Extra Large General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Extra Large General Service | 1 | 1
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)

## Ancillary Third Party
| Program Option: | Ancillary Third Party |  | Market PotentialWA | Market PotentialID |  | Base Year Peak Usage per Customer (kW) | [7 empty] | 2020 Avista Market Assessment Commercial NEQ and Market Profiles
|  |  |  | Market Potential | Market Potential |  | WA | Summer | Winter |  |  |  |  | Soucre: | F:\AEG\Clients\Avista Energy\31380-40-00 Avista 2020 CPA\LoadMAP\2 - Commercial Models\A - Electric Models\3 - Avista 2020 Electric CPA COM NEQ Generator.xlsm | F:\AEG\Clients\Avista Energy\31380-40-00 Avista 2020 CPA\LoadMAP\0 - Documentation\2 - Commercial Inputs\1a - Avista 2020 WA Comm Mkt Profile v2 - from PAC.xlsx
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes | Residential | #REF! | #REF! |  |  |  |  | Segment | Saturation | WA Usage (GWh) | ID Usage (GWh) | WA % Usage | ID % Usage | WA | ID
|  |  |  | State | State |  | General Service | #REF! | #REF! |  |  |  |  | Large Office | 40% | 30.4669 | 10.0515 | 18.52% | 12.2%
|  |  |  | WA | ID |  | Large General Service | #REF! | #REF! |  |  |  |  | Small Office | 0% | 12.7859 | 12.3545 | 7.772% | 15%
| ParticipationRate | [5 empty] | Extra Large General Service | #REF! | #REF! |  |  |  |  | Retail | 21% | 23.6633 | 12.1722 | 14.38% | 14.77%
Large General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Large General Service | 2.737% | 2.16% | Participation rate based on 2020 EE Study saturations of EMS systems within Avista commercial customers, weighted by segment size. | ID | [6 empty] | Restaurant | 2% | 2.86 | 0.83037 | 1.738% | 1.008%
Large General ServiceProgram ramp up period | Program ramp up period | Years | Large General Service | 3 | 3 |  | Residential | #REF! | #REF! |  |  |  |  | Grocery | 2.5% | 4.6158 | 0.22765 | 2.806% | 0.2763%
Large General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Large General Service | 1% | 1% |  | General Service | #REF! | #REF! |  |  |  |  | Health | 69% | 5.2982 | 2.6405 | 3.22% | 3.205%
[7 empty] | Large General Service | #REF! | #REF! |  |  |  |  | College | 63% | 7.3005 | 4.6221 | 4.437% | 5.61%
| ImpactInput | [5 empty] | Extra Large General Service | #REF! | #REF! |  |  |  |  | School | 24% | 16.6693 | 0.6103 | 10.13% | 0.7408%
Large General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | Large General Service | 0% | 0% | [8 empty] | Lodging | 6% | 7.2765 | 6.4544 | 4.423% | 7.834%
Large General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Large General Service | 15.75% | 15.75% | 75% of impact for ancillary | QC- impacts/customer | WA | ID |  |  |  |  | Warehouse | 0% | 20.8416 | 12.082 | 12.67% | 14.66%
Large General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Large General Service | 0 | 0 |  | Summer | #REF! | #REF! |  |  |  |  | Miscellaneous | 0% | 32.7424 | 20.3443 | 19.9% | 24.69%
Large General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Large General Service | 15.75% | 15.75% | 75% of impact for ancillary | Winter | #REF! | #REF!
Large General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Large General Service | 0 | 0
CEInput
Large General ServiceProgram Development Cost | Program Development Cost | $/program | Large General Service | 0 | 0 | No startup costs; Would be included in 3rd Party Costs |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
Large General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Large General Service | 0 | 0
Large General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Large General Service | 0 | 0 |  |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
Large General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Large General Service | 0 | 0 | Assume 3rd-party program delivery cost of $80/kW (60-80$/kW range). Additional 1% cost for utility overhead/admin costs.
Large General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost |  |  |  | Table to Allocate Program Admin Cost
Large General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost |  |  |  | 60000
Large General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Large General Service | 40000 | 40000 | Half for Ancillary |  |  |  | Table to Allocate Program Development Cost
Large General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost |  |  |  | 75000
Large General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost |  |  |  |  | WA | ID
Large General ServiceAMI Cost | AMI Cost | $/program/year | Large General Service | 0 | 0 |  |  |  |  | Residential | 0% | 0%
Large General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | Large General Service | 30 | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  |  |  | General Service | 9.65% | 3.567%
Large General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | Large General Service | 30 | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event. |  |  |  | Large General Service | 49.19% | 15.41%
Large General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost. Capacity reserve incentive pmt given to customers typically in range of $10 to $70 per kW-year |  |  |  | Extra Large General Service | 14.69% | 7.499%
Large General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost. Capacity reserve incentive pmt given to customers typically in range of $10 to $70 per kW-year
Large General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Large General Service | 0 | 0 |  |  |  |  | Total | 73.53% | 26.47% | 100%
Large General ServiceProgram Life | Program Life | years | Large General Service | 3 | 3
Large General ServiceProgram Start Year | Program Start Year | year | Large General Service | 2026 | 2028
Large General ServiceDe-rate | De-rate | capacity equivalence factor | Large General Service | 1 | 1
Large General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Large General Service | 1 | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
Extra Large General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Extra Large General Service | 2.737% | 2.16% | Participation rate based on 2020 EE Study saturations of EMS systems within Avista commercial customers, weighted by segment size.
Extra Large General ServiceProgram ramp up period | Program ramp up period | Years | Extra Large General Service | 3 | 3
Extra Large General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Extra Large General Service | 1% | 1%
ImpactInput
Extra Large General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | Extra Large General Service | 0% | 0%
Extra Large General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Extra Large General Service | 15.75% | 15.75% | 75% of impact for ancillary | QC- impacts/customer | WA | ID
Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Extra Large General Service | 0 | 0 |  | Summer | #REF! | #REF!
Extra Large General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Extra Large General Service | 15.75% | 15.75% | 75% of impact for ancillary | Winter | #REF! | #REF!
Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Extra Large General Service | 0 | 0
CEInput
Extra Large General ServiceProgram Development Cost | Program Development Cost | $/program | Extra Large General Service | 0 | 0 | No startup costs; Would be included in 3rd Party Costs
Extra Large General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Extra Large General Service | 0 | 0
Extra Large General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Extra Large General Service | 0 | 0
Extra Large General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Extra Large General Service | 0 | 0 | Assume 3rd-party program delivery cost of $80/kW (60-80$/kW range). Additional 1% cost for utility overhead/admin costs.
Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Extra Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost
Extra Large General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | Extra Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost
Extra Large General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Extra Large General Service | 40000 | 40000 | Half for Ancillary
Extra Large General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | Extra Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost
Extra Large General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Extra Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost
Extra Large General ServiceAMI Cost | AMI Cost | $/program/year | Extra Large General Service | 0 | 0
Extra Large General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | Extra Large General Service | 30 | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event.
Extra Large General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | Extra Large General Service | 30 | 30 | 30 hours is based on program experience as gathered during 2015 study. Pretty low on the spectrum for these programs, which can often have up to 60-100 hrs of event.
Extra Large General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Extra Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost. Capacity reserve incentive pmt given to customers typically in range of $10 to $70 per kW-year
Extra Large General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Extra Large General Service | 0 | 0 | included in 3rd Party Program Admin Cost. Capacity reserve incentive pmt given to customers typically in range of $10 to $70 per kW-year
Extra Large General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Extra Large General Service | 0 | 0
Extra Large General ServiceProgram Life | Program Life | years | Extra Large General Service | 3 | 3
Extra Large General ServiceProgram Start Year | Program Start Year | year | Extra Large General Service | 2026 | 2028
Extra Large General ServiceDe-rate | De-rate | capacity equivalence factor | Extra Large General Service | 1 | 1
Extra Large General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Extra Large General Service | 1 | 1
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)
Program Development Cost (per MW basis) | Program Development Cost (per MW basis)

## Thermal Energy Storage
| Program Option: | Thermal Energy Storage |  | Market PotentialWA | Market PotentialID |  |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes |  | Residential | #REF! | #REF!
|  |  |  | State | State |  |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  |  | Large General Service | #REF! | #REF!
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 0.5% | 0.5% | Don't expect much participation - 0.5% |  | Extra Large General Service | #REF! | #REF!
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 5 | 5 |  |  | ID
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1% | 1% |  |  | Residential | #REF! | #REF!
[8 empty] | General Service | #REF! | #REF!
| ImpactInput | [6 empty] | Large General Service | #REF! | #REF!
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 0% | 0% |  |  | Extra Large General Service | #REF! | #REF!
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 1.68 | 1.68 | Ice Energy - Ice Bear Tech Specifications, https://www.ice-energy.com/wp-content/uploads/2016/03/ICE-BEAR-30-Product-Sheet.pdf |  | QC- impacts/customer | WA | ID
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service |  |  |  |  | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service | 0 | 0 | Removed Winter Impacts |  | Winter | #REF! | #REF!
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | 24086.7793 | 18015.5463 | Share of Cost as noted in table at right
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | - | - | [5 empty] | # FTEs per program- refer to Admin Costs and AssumptionsTab
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | 19269.4234 | 14412.4371 | Share of Cost as noted in table at right
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | - | - | [5 empty] | Allocation based on share of 2042 (20-year) Summer MW potential
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 100 | 100 | Assumption $100 for RAP C&I, MAP = RAPx1.2
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 84 | 84 | Assumption of 5% equipment costs |  |  |  |  | Table to Allocate Program Admin Cost
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0 | 0 | [5 empty] | 60000
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 0 | 0 | [5 empty] | Table to Allocate Program Development Cost
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 1680 | 1680 | Utility Dive Article, Ice Energy Implementer cost |  |  |  |  | 75000
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0 | 0 | [6 empty] | WA | ID
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 36 | 36 | Same as TOU, six hours on peak period each summer |  |  |  |  | Residential | 0% | 0%
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | [7 empty] | General Service | 32.12% | 24.02%
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0 | 0 | [5 empty] | Large General Service | 29.42% | 13.9%
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0 | 0 | [5 empty] | Extra Large General Service | 0.3563% | 0.1866%
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 0 | 0 | No incentive. Program purchases & installs unit.
General ServiceProgram Life | Program Life | years | General Service | 20 | 20 | [5 empty] | Total | 61.89% | 38.11% | 100%
General ServiceProgram Start Year | Program Start Year | year | General Service | 2026 | 2026
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1 | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1 | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
Large General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Large General Service | 1.5% | 1.5% | Low participation is 1/2 DLC CAC | *Same as Small C&I
Large General ServiceProgram ramp up period | Program ramp up period | Years | Large General Service | 5 | 5
Large General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Large General Service | 1% | 1%
ImpactInput
Large General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | Large General Service | 0% | 0%
Large General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Large General Service
Large General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Large General Service | 8.4 | 8.4 | Ice Energy - Ice Bear Tech Specifications, https://www.ice-energy.com/wp-content/uploads/2016/03/ICE-BEAR-30-Product-Sheet.pdf |  | QC- impacts/customer | WA | ID
Large General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Large General Service |  |  |  |  | Summer | #REF! | #REF!
Large General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Large General Service |  |  | Removed Winter Impacts |  | Winter | #REF! | #REF!
CEInput
Large General ServiceProgram Development Cost | Program Development Cost | $/program | Large General Service | 22066.6033 | 10423.8736 | Share of Cost as noted in table at right
Large General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Large General Service | - | -
Large General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Large General Service | 17653.2826 | 8339.0989 | Share of Cost as noted in table at right
Large General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Large General Service | - | -
Large General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Large General Service | 100 | 100 | Assumption $100 for RAP C&I, MAP = RAPx1.2
Large General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | Large General Service | 420 | 420 | Assumption of 5% equipment costs
Large General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Large General Service | 0 | 0
Large General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | Large General Service | 0 | 0
Large General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Large General Service | 8400 | 8400 | Utility Dive Article, Ice Energy Implementer cost
Large General ServiceAMI Cost | AMI Cost | $/program/year | Large General Service | 0 | 0
Large General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | Large General Service | 36 | 36 | Same as TOU, six hours on peak period each summer
Large General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | Large General Service
Large General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Large General Service | 0 | 0
Large General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Large General Service | 0 | 0
Large General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Large General Service | 0 | 0 | No incentive. Program purchases & installs unit.
Large General ServiceProgram Life | Program Life | years | Large General Service | 20 | 20
Large General ServiceProgram Start Year | Program Start Year | year | Large General Service | 2026 | 2026
Large General ServiceDe-rate | De-rate | capacity equivalence factor | Large General Service | 1 | 1
Large General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Large General Service | 1 | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
Extra Large General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Extra Large General Service | 1.5% | 1.5% | Low participation is 1/2 DLC CAC | *Same as General Service
Extra Large General ServiceProgram ramp up period | Program ramp up period | Years | Extra Large General Service | 5 | 5
Extra Large General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Extra Large General Service | 1% | 1%
ImpactInput
Extra Large General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | Extra Large General Service | 0% | 0%
Extra Large General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Extra Large General Service
Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Extra Large General Service | 8.4 | 8.4 | Ice Energy - Ice Bear Tech Specifications, https://www.ice-energy.com/wp-content/uploads/2016/03/ICE-BEAR-30-Product-Sheet.pdf |  | QC- impacts/customer | WA | ID
Extra Large General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Extra Large General Service |  |  |  |  | Summer | #REF! | #REF!
Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Extra Large General Service |  |  | Removed Winter Impacts |  | Winter | #REF! | #REF!
CEInput
Extra Large General ServiceProgram Development Cost | Program Development Cost | $/program | Extra Large General Service | 267.2234 | 139.9741 | Share of Cost as noted in table at right
Extra Large General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Extra Large General Service | - | -
Extra Large General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Extra Large General Service | 213.7787 | 111.9793 | Share of Cost as noted in table at right
Extra Large General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Extra Large General Service | - | -
Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Extra Large General Service | 100 | 100 | Assumption $100 for RAP C&I, MAP = RAPx1.2
Extra Large General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | Extra Large General Service | 420 | 420 | Assumption of 5% equipment costs
Extra Large General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Extra Large General Service | 0 | 0
Extra Large General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | Extra Large General Service | 0 | 0
Extra Large General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Extra Large General Service | 8400 | 8400 | Utility Dive Article, Ice Energy Implementer cost
Extra Large General ServiceAMI Cost | AMI Cost | $/program/year | Extra Large General Service | 0 | 0
Extra Large General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | Extra Large General Service | 36 | 36 | Same as TOU, six hours on peak period each summer
Extra Large General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | Extra Large General Service
Extra Large General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Extra Large General Service | 0 | 0
Extra Large General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Extra Large General Service | 0 | 0
Extra Large General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Extra Large General Service | 0 | 0 | No incentive. Program purchases & installs unit.
Extra Large General ServiceProgram Life | Program Life | years | Extra Large General Service | 20 | 20
Extra Large General ServiceProgram Start Year | Program Start Year | year | Extra Large General Service | 2026 | 2026
Extra Large General ServiceDe-rate | De-rate | capacity equivalence factor | Extra Large General Service | 1 | 1
Extra Large General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Extra Large General Service | 1 | 1
Note on J26: Nielsen, Victoria: http://www.utilitydive.com/news/ice-ice-energy-the-hot-market-for-cooled-liquid-energy-storage/408356/ "The 100% turnkey service to utilities includes locating and signing customers, installing, commissioning, and doing all maintenance, Hopkins said. It is “about or just under $2,000/kW for a 20 year asset with minimal maintenance costs, about 1.5% per year."
Note on J63: Nielsen, Victoria: http://www.utilitydive.com/news/ice-ice-energy-the-hot-market-for-cooled-liquid-energy-storage/408356/ "The 100% turnkey service to utilities includes locating and signing customers, installing, commissioning, and doing all maintenance, Hopkins said. It is “about or just under $2,000/kW for a 20 year asset with minimal maintenance costs, about 1.5% per year."
Note on J101: Nielsen, Victoria: http://www.utilitydive.com/news/ice-ice-energy-the-hot-market-for-cooled-liquid-energy-storage/408356/ "The 100% turnkey service to utilities includes locating and signing customers, installing, commissioning, and doing all maintenance, Hopkins said. It is “about or just under $2,000/kW for a 20 year asset with minimal maintenance costs, about 1.5% per year."

## Battery Energy Storage
| Program Option: | Battery Energy Storage |  | Market PotentialWA | Market PotentialID |  |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes |  | Residential | #REF! | #REF!
|  |  |  | State | State |  |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  |  | Large General Service | #REF! | #REF!
| ParticipationRate | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 7.436% | 7.436% | PAC saw ~2.23% of solar PV customers participate in a battery DR program in year 2 of the program. (https://www.pacificorp.com/content/dam/pcorp/documents/en/pacificorp/environment/dsm/utah/2022_Utah_Wattsmart_Business_Energy_Eff_Peak_Reduction.pdf), solar PV # from DNV PG Study |  | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 5 | 5 | 2023 PAC CPA |  | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 0% | 0% | Huge buy in and capital cost will probably not have attrition/dropout |  | General Service | #REF! | #REF!
[8 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 0% | 0%
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential |  |  |  |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential | 2.23 | 1.85 | NREL 2021: 5 kW battery * 86% round trip efficiency. Xcel Energy CO Renewable Battery Connect: 40% retention |  | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential |  |  |  |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential | 2.58 | 2.44 | NREL 2021: 5 kW battery * 86% round trip efficiency. Xcel Energy CO Renewable Battery Connect: 40% retention
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | 41900.3699 | 22841.5283 | [5 empty] | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | - | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | 33520.2959 | 18273.2226 | half FTE @ $150,000 |  |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential | - | -
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 50 | 50 | [5 empty] | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 50 | 50 | 2023 PAC CPA: PNNL 2019 ($10/kW per year) |  |  |  |  | 60000
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | [7 empty] | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 2500 | 2500 | Xcel Energy CO Renewable Battery Connect: $500/enrolled kW for enrolling in the program (capped at 50% of battery equipment costs) |  |  |  |  | 75000
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | 0 | [6 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | 0 | Zero - at device level |  |  |  |  | Residential | 55.87% | 30.46%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 120 | 120 | Xcel Energy CO Renewable Battery Connect: up to 60 events per year, assuming 4-hr events. |  |  |  |  | General Service | 8.2% | 5.4%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 120 | 120 | Xcel Energy CO Renewable Battery Connect: up to 60 events per year, assuming 4-hr events. | 80% |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential | 0 | 0 | [5 empty] | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0 | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 0 | 0 | [5 empty] | Total | 64.07% | 35.86% | 99.92%
ResidentialProgram Life | Program Life | years | Residential | 15 | 15 | NREL
ResidentialProgram Start Year | Program Start Year | year | Residential | 2026 | 2026
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1 | 1
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1 | 1 | [13 empty] | Assume initially that Avista pays rebate for 30% of unit
[12 empty] | total peak kW per customer | Battery kWh capacity per customer | Battery kW per customer (DR impact) | lifetime (both program & equip) | assumed hrs used per day | cost per MWh | cost per kW | unit total cost | Annual MWh impacts | annual event hours
[11 empty] | Res | 2 ish | 12 | 2 | 8 | 6 | 1200 | 2628 | 5256 | 4.38 | 2190
[11 empty] | Small C&I | 2ish | 16 | 2 | 8 | 8 | 1200 | 3504 | 7008 | 5.84 | 2920
[11 empty] | Large C&I | 15 ish | 120 | 15 | 8 | 8 | 800 | 2336 | 35040 | 43.8 | 2920
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID | [7 empty] | Round Trip Battery Efficiency Notes
| ParticipationRate | [11 empty] | Assume: | 80%
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 7.436% | 7.436% | Same as Residential | [6 empty] | Technical Assessment for Maryland
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 15 | 15 | extending ramp up after 5 years because of battery storage's proven slow uptake. **changed to 15 years across low and high because it would be more expected than 10 & 20 years. | [6 empty] | http://energy.maryland.gov/Reports/FY15_Energy_Storage_Report.pdf
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 0% | 0% | Assume contracted to building | [6 empty] | - recommends 65% round trip efficiency requirement for batteries when designing a programs, value based empirical research in California
| ImpactInput | [11 empty] | Technical Assessment for California
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 0% | 0% | [7 empty] | http://www.energy.ca.gov/assessments/ab2514_reports/Turlock_Irrigation_District/2014-10-28_Turlock_Irrigation_District_Energy_Storage_Study.pdf
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service |  |  |  |  | QC- impacts/customer | WA | ID |  |  | - lithium Ion Batteries – round trip efficiency of 83%
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 2.58 | 2.58 | NREL 2021: 5 kW battery * 86% round trip efficiency. Xcel Energy CO Renewable Battery Connect: 40% retention |  | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service |  |  |  |  | Winter | #REF! | #REF! |  |  | Article on Storage Costs by power system company
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service | 2.58 | 2.58 | NREL 2021: 5 kW battery * 86% round trip efficiency. Xcel Energy CO Renewable Battery Connect: 40% retention | [6 empty] | http://www.imergy.com/blog/2015/1/the-true-cost-of-storage
- states that most batteries have a round trip efficiency of 75% or more
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | 6150 | 4050 | [7 empty] | Article on Li-ions
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | - | - | [7 empty] | http://www.pv-magazine.com/archive/articles/beitrag/advancing-li-ion-_100006681/501/#axzz4H21f2BpW
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | 4920 | 3240 | half FTE @ $150,000 | [6 empty] | - research done by Sandia National Laboratories (DOE) suggests Li-ion have round trip efficiencies of 85%
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | - | - | Calculated
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 50 | 50
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 50 | 50 | 2023 PAC CPA: PNNL 2019 ($10/kW per year)
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 2500 | 2500 | Xcel Energy CO Renewable Battery Connect: $500/enrolled kW for enrolling in the program (capped at 50% of battery equipment costs)
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0 | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0 | 0 | Zero - at device level
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 120 | 120 | Xcel Energy CO Renewable Battery Connect: up to 60 events per year, assuming 4-hr events.
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | 120 | 120 | Xcel Energy CO Renewable Battery Connect: up to 60 events per year, assuming 4-hr events. | 80%
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0 | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0 | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 0 | 0
General ServiceProgram Life | Program Life | years | General Service | 15 | 15 | NREL
General ServiceProgram Start Year | Program Start Year | year | General Service | 2026 | 2026 | Assumed rollout could piggyback on Utility's TOU
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1 | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1 | 1
Note on F14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Capped at 2.23kW which is the max household kW in Avista
Note on H14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Capped at 1.85 (max HH load)
Note on J14: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: https://atb.nrel.gov/electricity/2021/residential_battery_storage#T2TIPMSS
Note on H16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Capped at 2.44 (max HH load)
Note on J16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: https://atb.nrel.gov/electricity/2021/residential_battery_storage#T2TIPMSS
Note on J34: Duer, Anthony: https://www.nrel.gov/docs/fy16osti/64987.pdf
Note on J54: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: https://atb.nrel.gov/electricity/2021/residential_battery_storage#T2TIPMSS
Note on J56: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: https://atb.nrel.gov/electricity/2021/residential_battery_storage#T2TIPMSS
Note on J74: Duer, Anthony: https://www.nrel.gov/docs/fy16osti/64987.pdf

## Ancillary Battery Storage
| Program Option: | Ancillary Battery Storage |  | Market PotentialWA | Market PotentialID |  |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes |  | Residential | #REF! | #REF!
|  |  |  | State | State |  |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  |  | Large General Service | #REF! | #REF!
| ParticipationRate | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 0.5% | 0.5% | 20% from MISO LRZ 7. Assuming half for high and half again for low. *halved again 9-14-17, as per discussion with Kelly - potential looked too high. Pacificorp study didn't consider this program |  | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 15 | 15 | extending ramp up after 5 years because of battery storage's proven slow uptake. **changed to 15 years across low and high because it would be more expected than 10 & 20 years. |  | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 0% | 0% | Huge buy in and capital cost will probably not have attrition/dropout |  | General Service | #REF! | #REF!
[8 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 0% | 0%
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential |  |  |  |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential | 2.23 | 1.85 | Typical battery size for segment | 100% impact | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential |  |  |  |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential | 2.58 | 2.44 | Typical battery size for segment
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | 41900.3699 | 22841.5283 | [5 empty] | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | - | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | 33520.2959 | 18273.2226 | half FTE @ $150,000 |  |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential | - | -
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 50 | 50 | [5 empty] | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 0 | 0 | [5 empty] | 60000
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | [7 empty] | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 0 | 0 | Customer already has device if on program |  |  |  |  | 75000
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | 0 | [6 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | 0 | Zero - at device level |  |  |  |  | Residential | 55.87% | 30.46%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 36 | 36 | [5 empty] | General Service | 8.2% | 5.4%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 36 | 36 | Round trip efficiency assumption: | 80% |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential | 0 | 0 | [5 empty] | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0 | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 20 | 20 | $20 incentives to participate in ancillary |  |  |  |  | Total | 64.07% | 35.86% | 99.92%
ResidentialProgram Life | Program Life | years | Residential | 15 | 15 | NREL
ResidentialProgram Start Year | Program Start Year | year | Residential | 2026 | 2026
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1 | 1
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1 | 1 | [13 empty] | Assume initially that Avista pays rebate for 30% of unit
[12 empty] | total peak kW per customer | Battery kWh capacity per customer | Battery kW per customer (DR impact) | lifetime (both program & equip) | assumed hrs used per day | cost per MWh | cost per kW | unit total cost | Annual MWh impacts | annual event hours
[11 empty] | Res | 2 ish | 12 | 2 | 8 | 6 | 1200 | 2628 | 5256 | 4.38 | 2190
[11 empty] | Small C&I | 2ish | 16 | 2 | 8 | 8 | 1200 | 3504 | 7008 | 5.84 | 2920
[11 empty] | Large C&I | 15 ish | 120 | 15 | 8 | 8 | 800 | 2336 | 35040 | 43.8 | 2920
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID | [7 empty] | Round Trip Battery Efficiency Notes
| ParticipationRate | [11 empty] | Assume: | 80%
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 0.5% | 0.5% | Same as Residential | [6 empty] | Technical Assessment for Maryland
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 15 | 15 | extending ramp up after 5 years because of battery storage's proven slow uptake. **changed to 15 years across low and high because it would be more expected than 10 & 20 years. | [6 empty] | http://energy.maryland.gov/Reports/FY15_Energy_Storage_Report.pdf
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 0% | 0% | Assume contracted to building | [6 empty] | - recommends 65% round trip efficiency requirement for batteries when designing a programs, value based empirical research in California
| ImpactInput | [11 empty] | Technical Assessment for California
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 0% | 0% | [7 empty] | http://www.energy.ca.gov/assessments/ab2514_reports/Turlock_Irrigation_District/2014-10-28_Turlock_Irrigation_District_Energy_Storage_Study.pdf
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service |  |  |  |  | QC- impacts/customer | WA | ID |  |  | - lithium Ion Batteries – round trip efficiency of 83%
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 2.58 | 2.58 | Typical battery size for segment |  | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service |  |  |  |  | Winter | #REF! | #REF! |  |  | Article on Storage Costs by power system company
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service | 2.58 | 2.58 | Typical battery size for segment | [6 empty] | http://www.imergy.com/blog/2015/1/the-true-cost-of-storage
- states that most batteries have a round trip efficiency of 75% or more
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | 6150 | 4050 | [7 empty] | Article on Li-ions
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | - | - | [7 empty] | http://www.pv-magazine.com/archive/articles/beitrag/advancing-li-ion-_100006681/501/#axzz4H21f2BpW
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | 4920 | 3240 | half FTE @ $150,000 | [6 empty] | - research done by Sandia National Laboratories (DOE) suggests Li-ion have round trip efficiencies of 85%
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | - | - | Calculated
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 50 | 50
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 0 | 0
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 0 | 0 | Customer already has device if on program
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0 | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0 | 0 | Zero - at device level
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 36 | 36
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | 36 | 36 | Round trip efficiency assumption: | 80%
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0 | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0 | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 20 | 20 | $20 incentives to participate in ancillary
General ServiceProgram Life | Program Life | years | General Service | 15 | 15 | NREL
General ServiceProgram Start Year | Program Start Year | year | General Service | 2026 | 2026 | Assumed rollout could piggyback on Utility's TOU
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1 | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1 | 1
Note on J34: Duer, Anthony: https://www.nrel.gov/docs/fy16osti/64987.pdf
Note on J74: Duer, Anthony: https://www.nrel.gov/docs/fy16osti/64987.pdf

## Behavioral
| Program Option: | Behavioral |  | Market PotentialWA | Market PotentialID |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes | Residential | #REF! | #REF!
|  |  |  | State | State |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  | Large General Service | #REF! | #REF!
| ParticipationRate | [5 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 20% | 20% | high rate based on PG&E rollout with six waves http://www.calmac.org/publications/DNVGL_PGE_HERs_2015_final_to_calmac.pdf --> PC study has high case at 20% | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 3 | 3 |  | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 2% | 2% | Between Consumers (3%) and DTE(1%) | General Service | #REF! | #REF!
[7 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [5 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 0% | 0%
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential | 2% | 2% | Opower documentation for BDR with Consumers and DTE | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential |  |  | hi participation case = 0.75% of low to account for lower potential customers | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential | 2% | 2% |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | 66832.372 | 33167.628 |  |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | 40099.4232 | 19900.5768 |  |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 0 | 0 |  |  |  |  | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 3.25 | 3.25 | Oracle interview on 8/30, estimation of admin cost per household - KM heard 3 - 3.5 all inclusive- Implementation Cost |  |  |  | 60000
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | 0 |  |  |  |  | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 0 | 0 |  |  |  |  | 100000
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | 0 | [5 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | 0 | No AMI Cost as a part of DR program costs |  |  |  | Residential | 66.83% | 33.17%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 40 | 40 | 8 hour event window x 5 events, Consumers Energy 7am-8pm 8 hr window |  |  |  | General Service | 0% | 0%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 40 | 40 | 8 hour event window x 5 events, Consumers Energy 7am-8pm 8 hr window |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential | 0 | 0 |  |  |  |  | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0 | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 0 | 0 | No Incentive for Behavioral DR - Brattle PGE Potential Study 2016 - |  |  |  | Total | 66.83% | 33.17% | 100%
ResidentialProgram Life | Program Life | years | Residential | 1 | 1 | MISO Res LoadMAP DSM Programs.xlsx (LRZ7) - Lifetime
ResidentialProgram Start Year | Program Start Year | year | Residential | 2026 | 2026
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1 | 1 | Impact Reduced to reflect diminished savings program pulls in participants who are not "high" users
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1 | 1
|  |  |  | #N/A | #N/A
| Program Development Cost | 0 | 0
|  |  |  | #N/A | #N/A

## Pilot-Time-of-Use Opt-In (hidden)
| Program Option: | Time-of-Use Opt-in |  | Market PotentialWA | Market PotentialID |  |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes |  | Residential | #REF! | #REF!
|  |  |  | State | State |  |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  |  | Large General Service | #REF! | #REF!
| ParticipationRate | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 0.41% |  | Modified for pilot scope | Brattle Northern States Study | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 3.5 |  |  | Opt‐in participation- expected to result in 5% to 25% enrollment | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 1% |  |  | Opt‐out participation- typically expected to result in 50% to 90% enrollment | General Service | #REF! | #REF!
[8 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 0% |  | None - should be in eval'd number.
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential | 5.7% |  | Brattle Analysis and Estimate - Pacificorp 2019 opt-in and opt-out scenarios |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential |  |  |  |  | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential | 2.85% |  | Assume 50% of Summer impacts. Brattle Analysis and Estimate - Negative impacts in Winter set to zero in Eastern states. |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential | 0
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | 537510.0049 | [6 empty] | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | 53751.0005 | [6 empty] | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential | -
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 50 |  | 1.5x standatd $50 marketing cost because it involves more education on kW rate blocks |  |  |  |  | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 0 | [6 empty] | 100000
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | [6 empty] | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 0 | [6 empty] | 1000000
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | [7 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 |  | If installed prior to Default AMI Rollout (indicated by Program Start Year), assume $177 cost for TOU meter ($162 from spreadsheet + $15 from email) [see Eli email 2/2/2016] |  |  |  |  | Residential | 53.75% | 26.68%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 528 |  | Six hours on-peak period each summer weekday |  |  |  |  | General Service | 13.36% | 6.216%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 528 |  | Six hours on-peak period each winter weekday too, except for Utah |  |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential | 0 | [6 empty] | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 0 |  | Incentive built into rate design |  |  |  |  | Total | 67.11% | 32.89% | 100%
ResidentialProgram Life | Program Life | years | Residential | 10
ResidentialProgram Start Year | Program Start Year | year | Residential | 2024 |  | Modeling potential pilot starting in 2024
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 0.41% |  | Modified for pilot scope
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 3.5
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1% |  | Consumer's DR Program
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 0%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service | 0.2% |  | Brattle Analysis and Estimate - Pacificorp 2019 opt-in and opt-out scenarios |  | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 0 |  |  |  | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service | 0.1% |  | Assume 50% of Summer impacts. |  | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service | 0
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | 133578.494
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | 13357.8494
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | -
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 60 |  | 1.5x standatd $50 marketing cost because it involves more education on kW rate blocks
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 0
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 0
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0 |  | If installed prior to Default AMI Rollout (indicated by Program Start Year), assume $220 for TOU meter ($245 from spreadsheet - $25 from email) [see Eli email 2/2/2016]
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 528 |  | Six hours on-peak period each summer weekday
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | 528 |  | Six hours on-peak period each winter weekday too, except for Utah
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 0 |  | Incentive built into rate design
General ServiceProgram Life | Program Life | years | General Service | 10
General ServiceProgram Start Year | Program Start Year | year | General Service | 2024 |  | Modeling potential pilot starting in 2024
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1
Note on J15: Nguyen, Fuong: Rationale here is that we assume summer impacts will include HVAC impacts, however, not all participants have electric heat, and with no eligibility around electric heat, it does not make sense that you would see the same % reduction in the winter since there is less potential load to curtail in primarily gas homes.
Note on J53: Nguyen, Fuong: Rationale here is that we assume summer impacts will include HVAC impacts, however, not all participants have electric heat, and with no eligibility around electric heat, it does not make sense that you would see the same % reduction in the winter since there is less potential load to curtail in primarily gas homes.

## Parent-Time-of-Use Opt-In
| Program Option: | Time-of-Use Opt-in |  | Market PotentialWA | Market PotentialID |  |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes |  | Residential | #REF! | #REF!
|  |  |  | State | State |  |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  |  | Large General Service | #REF! | #REF!
| ParticipationRate | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 13% | 13% | Brattle Analysis and Estimate | Brattle Northern States Study | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 5 | 5 | 2024 Avista Update | Opt‐in participation- expected to result in 5% to 25% enrollment | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 1% | 1% |  | Opt‐out participation- typically expected to result in 50% to 90% enrollment | General Service | #REF! | #REF!
[8 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 0% | 0% | None - should be in eval'd number.
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential | 4% | 4% | 2024 Avista Update |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential |  |  |  |  | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential | 1.5% | 1.5% | 2024 Avista Update |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential | 0 | 0
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | 0 | 811026.4756 | 2024 Avista Update- WA dev costs are sunk($2 mil), ID costs will be half of WA @ $1mil dev costs |  |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | - | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | 134382.8763 | 66691.6514 | 2024 Avista Update |  |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential | - | -
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 60 | 60 | 2024 Avista Update | 1.5x standatd $50 marketing cost because it involves more education on kW rate blocks |  |  |  | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 0 | 0 | [5 empty] | 250010 | 2024 Avista Update: + $10 for comminications + $150,000 for web presentation ventor/year
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | 0 | [5 empty] | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 0 | 0 | [5 empty] | 1000000
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | 0 | [6 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | 0 | If installed prior to Default AMI Rollout (indicated by Program Start Year), assume $177 cost for TOU meter ($162 from spreadsheet + $15 from email) [see Eli email 2/2/2016] |  |  |  |  | Residential | 53.75% | 26.68% |  | 81.1%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 528 | 528 | Six hours on-peak period each summer weekday |  |  |  |  | General Service | 13.36% | 6.216% |  | 18.9%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 528 | 528 | Six hours on-peak period each winter weekday too, except for Utah |  |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential | 0 | 0 | [5 empty] | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0 | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 0 | 0 | Incentive built into rate design |  |  |  |  | Total | 67.11% | 32.89% | 100%
ResidentialProgram Life | Program Life | years | Residential | 10 | 10
ResidentialProgram Start Year | Program Start Year | year | Residential | 2025 | 2028 | WA; ID Start in 2028: 2024 Avista Update; will change ramp rate after model run
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1 | 1
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1 | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 7% | 7% | 2024 Avista Update
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 5 | 5 | Pacificorp. MISO used 1 year.
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1% | 1% | Consumer's DR Program
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 0% | 0%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service | 0.2% | 0.2% | Brattle Analysis and Estimate - Pacificorp 2019 opt-in and opt-out scenarios |  | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 0 | 0 |  |  | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service | 0.1% | 0.1% | Assume 50% of Summer impacts. |  | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service | 0 | 0
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | 133578.494 | 188973.5244 | 2024 Avista Update- WA dev costs are sunk($2 mil), ID costs will be half of WA @ $1mil dev costs
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | - | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | 33395.9593 | 15539.513 | 2024 Avista Update
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | - | -
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 60 | 60 | 2024 Avista Update | 1.5x standatd $50 marketing cost because it involves more education on kW rate blocks
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 0 | 0
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0 | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 0 | 0
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0 | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0 | 0 | If installed prior to Default AMI Rollout (indicated by Program Start Year), assume $220 for TOU meter ($245 from spreadsheet - $25 from email) [see Eli email 2/2/2016]
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 528 | 528 | Six hours on-peak period each summer weekday
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | 528 | 528 | Six hours on-peak period each winter weekday too, except for Utah
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0 | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0 | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 0 | 0 | Incentive built into rate design
General ServiceProgram Life | Program Life | years | General Service | 10 | 10
General ServiceProgram Start Year | Program Start Year | year | General Service | 2025 | 2028 | WA; ID Start in 2028: 2024 Avista Update; will change ramp rate after model run
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1 | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1 | 1
Note on J15: Nguyen, Fuong: Rationale here is that we assume summer impacts will include HVAC impacts, however, not all participants have electric heat, and with no eligibility around electric heat, it does not make sense that you would see the same % reduction in the winter since there is less potential load to curtail in primarily gas homes.
Note on O26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Removed Development costs from parent program. Modeling up-front costs in the pilot Reply: For "Considered" program scenario, all costs stay in parents. No pilots.
Note on J55: Nguyen, Fuong: Rationale here is that we assume summer impacts will include HVAC impacts, however, not all participants have electric heat, and with no eligibility around electric heat, it does not make sense that you would see the same % reduction in the winter since there is less potential load to curtail in primarily gas homes.

## Time-of-Use Opt-Out
| Program Option: | Time-of-Use Opt-Out |  | Market PotentialWA | Market PotentialID |  |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes |  | Residential | #REF! | #REF!
|  |  |  | State | State |  |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  |  | Large General Service | #REF! | #REF!
| ParticipationRate | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 20% | 20% | 2024 Avista Update | Brattle Northern States Study | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 5 | 5 |  | Opt‐in participation- expected to result in 5% to 25% enrollment | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 1% | 1% |  | Opt‐out participation- typically expected to result in 50% to 90% enrollment | General Service | #REF! | #REF!
[8 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [6 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 0% | 0% | None - should be in eval'd number.
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential | 1.5% | 1.5% | 2024 Avista Update |  | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential |  |  |  |  | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential | 0.2% | 0.2% | 2024 Avista Update |  | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential | 0 | 0
CEInput
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | 711991.4105 | 353347.7202 | 2024 Avista Update |  |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | - | -
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | 118669.9817 | 58893.6424 | 2024 Avista Update |  |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential | - | -
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 60 | 60 | 2024 Avista Update | 1.5x standatd $50 marketing cost because it involves more education on kW rate blocks |  |  |  | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 0 | 0 | [5 empty] | 250010 | 2024 Avista Update: + $10 for comminications + $150,000 for web presentation ventor/year
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | 0 | [5 empty] | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 0 | 0 | [5 empty] | 1500000 | 2024 Avista Updates: TOU Opt-Out is $500,000 more expensive
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | 0 | [6 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | 0 | If installed prior to Default AMI Rollout (indicated by Program Start Year), assume $177 cost for TOU meter ($162 from spreadsheet + $15 from email) [see Eli email 2/2/2016] |  |  |  |  | Residential | 47.47% | 23.56%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 528 | 528 | Six hours on-peak period each summer weekday |  |  |  |  | General Service | 19.78% | 9.202%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 528 | 528 | Six hours on-peak period each winter weekday too, except for Utah |  |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential | 0 | 0 | [5 empty] | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0 | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 0 | 0 | Incentive built into rate design |  |  |  |  | Total | 67.24% | 32.76% | 100%
ResidentialProgram Life | Program Life | years | Residential | 10 | 10
ResidentialProgram Start Year | Program Start Year | year | Residential | 2025 | 2028 | 2024 Avista Update
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1 | 1
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1 | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 20% | 20% | 2024 Avista Update
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 5 | 5 | Pacificorp. MISO used 1 year.
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1% | 1% | Consumer's DR Program
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 0% | 0%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service | 0.2% | 0.2% | Brattle Analysis and Estimate - Pacificorp 2019 opt-in and opt-out scenarios |  | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 0 | 0 |  |  | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service | 0.1% | 0.1% | Assume 50% of Summer impacts. |  | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service | 0 | 0
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | 296633.8329 | 138027.0364 | 2024 Avista Update
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | - | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | 49440.9497 | 23005.4262 | 2024 Avista Update
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | - | -
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 60 | 60 | 2024 Avista Update | 1.5x standatd $50 marketing cost because it involves more education on kW rate blocks
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 0 | 0
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0 | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 0 | 0
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0 | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0 | 0 | If installed prior to Default AMI Rollout (indicated by Program Start Year), assume $220 for TOU meter ($245 from spreadsheet - $25 from email) [see Eli email 2/2/2016]
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 528 | 528 | Six hours on-peak period each summer weekday
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | 528 | 528 | Six hours on-peak period each winter weekday too, except for Utah
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0 | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0 | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 0 | 0 | Incentive built into rate design
General ServiceProgram Life | Program Life | years | General Service | 10 | 10
General ServiceProgram Start Year | Program Start Year | year | General Service | 2025 | 2028
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1 | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1 | 1
Note on J15: Nguyen, Fuong: Rationale here is that we assume summer impacts will include HVAC impacts, however, not all participants have electric heat, and with no eligibility around electric heat, it does not make sense that you would see the same % reduction in the winter since there is less potential load to curtail in primarily gas homes.
Note on J55: Nguyen, Fuong: Rationale here is that we assume summer impacts will include HVAC impacts, however, not all participants have electric heat, and with no eligibility around electric heat, it does not make sense that you would see the same % reduction in the winter since there is less potential load to curtail in primarily gas homes.

## Electric Vehicle TOU Opt-In
| Program Option: | Electric Vehicle TOU Opt-in |  | Market PotentialWA | Market PotentialID |  |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Class not included in the final model- just a reference |  | Res-EV | 0.72264 | 0.72264 | 0.54198
|  |  |  | State | State |  |  | GS-EV | 0.72264 | 0.72264
|  |  |  | WA | ID |  |  | LGS-EV | 6.6667 | 6.6667
| ParticipationRate | [6 empty] | ELGS-EV | 6.6667 | 6.6667
GS-EVSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | GS-EV | 20% | 20% | 2024 Avista Update: sch 13 | Brattle Northern States Study | ID
GS-EVProgram ramp up period | Program ramp up period | Years | GS-EV | 5 | 5 | 2024 Avista Update |  | Res-EV | 0.72264 | 0.72264
GS-EVProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | GS-EV | 1% | 1% |  |  | GS-EV | 0.72264 | 0.72264
[8 empty] | LGS-EV | 6.6667 | 6.6667
| ImpactInput | [6 empty] | ELGS-EV | 6.6667 | 6.6667
GS-EVEvent Non-Performance Rate | Event Non-Performance Rate | % | GS-EV | 0% | 0%
GS-EVPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | GS-EV | 100% | 100% | 2024 Avista Update: of total EV load instead of total HH load | Brattle Analysis and Estimate, based on DTE rate differential of 2.5 | QC- impacts/customer | WA | ID
GS-EVPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | GS-EV | 0 | 0 |  |  | Summer | 0.72264 | 0.72264
GS-EVPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | GS-EV | 100% | 100% | 2024 Avista Update: of total EV load instead of total HH load | Brattle Analysis and Estimate, based on DTE rate differential of 2.5 | Winter | 0.72264 | 0.72264
GS-EVPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | GS-EV | 0 | 0
CEInput
GS-EVProgram Development Cost | Program Development Cost | $/program | GS-EV | 0 | 0 | [5 empty] | # FTEs per program- refer to Admin Costs and AssumptionsTab
GS-EVProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | GS-EV | - | -
GS-EVAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | GS-EV | 32916.248 | 23738.424 | [5 empty] | Allocation based on share of 2042 (20-year) Summer MW potential
GS-EVAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | GS-EV | - | -
GS-EVPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | GS-EV | 50 | 50 | 2024 Avista Update | 1.5x standatd $50 marketing cost because it involves more education on kW rate blocks |  |  |  | Table to Allocate Program Admin Cost
GS-EVAnnual O&M Cost | Annual O&M Cost | $/participant/year | GS-EV | 0 | 0 | [5 empty] | 75000
GS-EVAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | GS-EV | 0 | 0 | [5 empty] | Table to Allocate Program Development Cost
GS-EVCost of Equip + Install | Cost of Equip + Install | $/tech | GS-EV | 0 | 0 | [5 empty] | 0
GS-EVCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | GS-EV | 0 | 0 | [6 empty] | WA | ID
GS-EVAMI Cost | AMI Cost | $/program/year | GS-EV | 0 | 0 | [5 empty] | Res-EV | 0% | 0%
GS-EVSummer DR Event Hours | Summer DR Event Hours | hours/year | GS-EV | 528 | 528 | Six hours on-peak period each summer weekday |  |  |  |  | GS-EV | 43.89% | 31.65%
GS-EVWinter DR Event Hours | Winter DR Event Hours | hours/year | GS-EV | 528 | 528 | Six hours on-peak period each winter weekday too, except for Utah |  |  |  |  | LGS-EV | 16.48% | 7.981%
GS-EVPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | GS-EV | 0 | 0 | [5 empty] | ELGS-EV | 0% | 0%
GS-EVPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | GS-EV | 0 | 0
GS-EVPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | GS-EV | 0 | 0 | Incentive built into rate design |  |  |  |  | Total | 60.37% | 39.63% | 100%
GS-EVProgram Life | Program Life | years | GS-EV | 10 | 10
GS-EVProgram Start Year | Program Start Year | year | GS-EV | 2025 | 2025 | 2024 Avista Update | Metering capability exists in this class, but need 2 years before program can be implemented and ramp up. |  |  |  | State | Class | Peak Load
GS-EVDe-rate | De-rate | capacity equivalence factor | GS-EV | 1 | 1 | [5 empty] | WA | Res-EV | 1.2109
GS-EVNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | GS-EV | 1 | 1 | [5 empty] | ID | Res-EV | 0.62048
[11 empty] | WA | GS-EV | 0.57295
[11 empty] | ID | GS-EV | 0.4132
[11 empty] | WA | LGS-EV | 0.28093
| Data Element | Unit | Customer Class | Market Potential | Market Potential | [5 empty] | ID | LGS-EV | 0.13607
|  |  |  | State | State | [5 empty] | WA | ELGS-EV | 0.2773
|  |  |  | WA | ID | [5 empty] | ID | ELGS-EV | 0.1397
| ParticipationRate | [13 empty] | Summer |  |  |  |  | Winter
LGS-EVSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | LGS-EV | 10% | 10% | 2024 Avista Update: sch 23 | [5 empty] | DTE rate differential |  |  |  | Peak | Off-Peak | Differential | Impact |  | Peak | Off-Peak | Differential
LGS-EVProgram ramp up period | Program ramp up period | Years | LGS-EV | 5 | 5 | 2024 Avista Update |  |  |  |  | On-peak | 0.18 |  |  | BGE | 0.347 | 0.075 | 4.65 | 9% | BGE | 0.362 | 0.076 | 4.76
LGS-EVProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | LGS-EV | 1% | 1% | [5 empty] | Off-Peak | 0.07 | 2.5714 |  | Pepco | 0.399 | 0.091 | 4.38 | 8.5% | Pepco | 0.419 | 0.099 | 4.22
[12 empty] | Impact | 7% |  | DPL | 0.507 | 0.087 | 5.82 | 11% | DPL | 0.514 | 0.089 | 5.77
ImpactInput
LGS-EVEvent Non-Performance Rate | Event Non-Performance Rate | % | LGS-EV | 0% | 0%
LGS-EVPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | LGS-EV | 100% | 100% | 2024 Avista Update: of total EV load instead of total HH load | Brattle Analysis and Estimate, based on DTE rate differential of 2.5 | QC- impacts/customer | WA | ID
LGS-EVPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | LGS-EV | 0 | 0 |  |  | Summer | 6.6667 | 6.6667
LGS-EVPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | LGS-EV | 100% | 100% | 2024 Avista Update: of total EV load instead of total HH load | Brattle Analysis and Estimate, based on DTE rate differential of 2.5 | Winter | 6.6667 | 6.6667
LGS-EVPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | LGS-EV | 0 | 0
CEInput
LGS-EVProgram Development Cost | Program Development Cost | $/program | LGS-EV | 0 | 0
LGS-EVProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | LGS-EV | - | -
LGS-EVAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | LGS-EV | 12359.2575 | 5986.0705
LGS-EVAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | LGS-EV | - | -
LGS-EVPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | LGS-EV | 50 | 50 | 2024 Avista Update | 1.5x standatd $50 marketing cost because it involves more education on kW rate blocks
LGS-EVAnnual O&M Cost | Annual O&M Cost | $/participant/year | LGS-EV | 0 | 0
LGS-EVAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | LGS-EV | 0 | 0
LGS-EVCost of Equip + Install | Cost of Equip + Install | $/tech | LGS-EV | 0 | 0
LGS-EVCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | LGS-EV | 0 | 0
LGS-EVAMI Cost | AMI Cost | $/program/year | LGS-EV | 0 | 0 | All Large/XL C&I already have TOU meters. No additional cost. [see Eli email 2/2/2016]
LGS-EVSummer DR Event Hours | Summer DR Event Hours | hours/year | LGS-EV | 528 | 528 | Six hours on-peak period each summer weekday
LGS-EVWinter DR Event Hours | Winter DR Event Hours | hours/year | LGS-EV | 528 | 528 | Six hours on-peak period each winter weekday too, except for Utah
LGS-EVPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | LGS-EV | 0 | 0
LGS-EVPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | LGS-EV | 0 | 0
LGS-EVPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | LGS-EV | 0 | 0 | Incentive built into rate design
LGS-EVProgram Life | Program Life | years | LGS-EV | 10 | 10
LGS-EVProgram Start Year | Program Start Year | year | LGS-EV | 2025 | 2025 | 2024 Avista Update | Metering capability exists in this class, but need 2 years before program can be implemented and ramp up.
LGS-EVDe-rate | De-rate | capacity equivalence factor | LGS-EV | 1 | 1
LGS-EVNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | LGS-EV | 1 | 1

## Variable Peak Pricing Rates
| Program Option: | Variable Peak Pricing Rates |  | Market PotentialWA | Market PotentialID |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes | Residential | #REF! | #REF!
|  |  |  | State | State |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  | Large General Service | #REF! | #REF!
| ParticipationRate | [5 empty] | Extra Large General Service | #REF! | #REF!
Large General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Large General Service | 25% | 25% | High Case- OG&E's VPP Plus participation rate- should be 103000/400000 around 25% | ID
Large General ServiceProgram ramp up period | Program ramp up period | Years | Large General Service | 5 | 5 | Pacificorp. MISO used 1 year. | Residential | #REF! | #REF!
Large General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Large General Service | 1% | 1% |  | General Service | #REF! | #REF!
[7 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [5 empty] | Extra Large General Service | #REF! | #REF!
Large General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | Large General Service | 0% | 0%
Large General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Large General Service | 4% | 4% | OG&E 2017 Smart Hours Study - 4% for an average CPE day for VPP only customers without a smart thermostat | QC- impacts/customer | WA | ID
Large General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Large General Service | 0 | 0 |  | Summer | #REF! | #REF!
Large General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Large General Service | 3% | 3% |  | Winter | #REF! | #REF!
Large General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Large General Service | 0 | 0
CEInput
Large General ServiceProgram Development Cost | Program Development Cost | $/program | Large General Service | 39233.2746 | 15569.5434 |  |  |  |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
Large General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Large General Service | - | -
Large General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Large General Service | 39233.2746 | 15569.5434 |  |  |  |  | Allocation based on share of 2042 (20-year) Summer MW potential
Large General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Large General Service | - | -
Large General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Large General Service | 200 | 200 | Assumed 4X Residential recruitment costs of $50 |  |  |  | Table to Allocate Program Admin Cost
Large General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | Large General Service | 0 | 0 |  |  |  |  | 75000
Large General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Large General Service | 0 | 0 |  |  |  |  | Table to Allocate Program Development Cost
Large General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | Large General Service | 0 | 0 | No equipment cost because assuming they have their own technology (like a Energy Management System etc) to control their processes |  |  |  | 75000
Large General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Large General Service | 0 | 0 | Currently zero, but $360/kW if tech costs included. Based on Auto-DR tech enablement costs. $300/kW is incentive level offered by SCE for Auto-DR participants, and is expected to cover a large fraction of costs. 20% adder included to recognize some additional expenses on the part of the customer. |  |  |  |  | WA | ID
Large General ServiceAMI Cost | AMI Cost | $/program/year | Large General Service | 0 | 0 | All Large/XL C&I already have TOU meters. No additional cost. [see Eli email 2/2/2016] |  |  |  | Residential | 0% | 0%
Large General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | Large General Service | 40 | 40 | Top 40 summer system hours |  |  |  | General Service | 0% | 0%
Large General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | Large General Service | 40 | 40 | Using summer hours except for UT |  |  |  | Large General Service | 52.31% | 20.76%
Large General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Large General Service | 0 | 0 |  |  |  |  | Extra Large General Service | 16.35% | 10.58%
Large General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Large General Service | 0 | 0
Large General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Large General Service | 0 | 0 | Incentive built into rate design |  |  |  | Total | 68.66% | 31.34% | 100%
Large General ServiceProgram Life | Program Life | years | Large General Service | 10 | 10
Large General ServiceProgram Start Year | Program Start Year | year | Large General Service | 2026 | 2026 | Metering capability exists in this class, but need 2 years before program can be implemented and ramp up.
Large General ServiceDe-rate | De-rate | capacity equivalence factor | Large General Service | 1 | 1
Large General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Large General Service | 1 | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
Extra Large General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Extra Large General Service | 25% | 25% | High Case- OG&E's VPP Plus participation rate
Extra Large General ServiceProgram ramp up period | Program ramp up period | Years | Extra Large General Service | 5 | 5 | Pacificorp. MISO used 1 year.
Extra Large General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Extra Large General Service | 2% | 2% | Consumer's DR Program
ImpactInput
Extra Large General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | Extra Large General Service | 0% | 0%
Extra Large General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Extra Large General Service | 4% | 4% | OG&E 2017 Smart Hours Study - 4% for an average CPE day for VPP only customers without a smart thermostat | QC- impacts/customer | WA | ID
Extra Large General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Extra Large General Service | 0 | 0 |  | Summer | #REF! | #REF!
Extra Large General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Extra Large General Service | 3% | 3% |  | Winter | #REF! | #REF!
Extra Large General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Extra Large General Service | 0 | 0
CEInput
Extra Large General ServiceProgram Development Cost | Program Development Cost | $/program | Extra Large General Service | 12264.7425 | 7932.4396
Extra Large General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Extra Large General Service | - | -
Extra Large General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Extra Large General Service | 12264.7425 | 7932.4396
Extra Large General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Extra Large General Service | - | -
Extra Large General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Extra Large General Service | 400 | 400 | Assumed 2X Large C&I recruitment costs
Extra Large General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | Extra Large General Service | 0 | 0
Extra Large General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Extra Large General Service | 0 | 0
Extra Large General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | Extra Large General Service | 0 | 0
Extra Large General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Extra Large General Service | 0 | 0 | Currently zero, but $360/kW if tech costs included. Based on Auto-DR tech enablement costs. $300/kW is incentive level offered by SCE for Auto-DR participants, and is expected to cover a large fraction of costs. 20% adder included to recognize some additional expenses on the part of the customer.
Extra Large General ServiceAMI Cost | AMI Cost | $/program/year | Extra Large General Service | 0 | 0 | All Large/XL C&I already have TOU meters. No additional cost. [see Eli email 2/2/2016]
Extra Large General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | Extra Large General Service | 40 | 40 | Top 40 summer system hours
Extra Large General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | Extra Large General Service | 40 | 40 | Using summer hours except for UT
Extra Large General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Extra Large General Service | 0 | 0
Extra Large General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Extra Large General Service | 0 | 0
Extra Large General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Extra Large General Service | 0 | 0 | Incentive built into rate design
Extra Large General ServiceProgram Life | Program Life | years | Extra Large General Service | 10 | 10
Extra Large General ServiceProgram Start Year | Program Start Year | year | Extra Large General Service | 2026 | 2026 | Metering capability exists in this class, but need 2 years before program can be implemented and ramp up.
Extra Large General ServiceDe-rate | De-rate | capacity equivalence factor | Extra Large General Service | 1 | 1
Extra Large General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Extra Large General Service | 1 | 1
Note on J15: Nguyen, Fuong: Rationale here is that we assume summer impacts will include HVAC impacts, however, not all participants have electric heat, and with no eligibility around electric heat, it does not make sense that you would see the same % reduction in the winter since there is less potential load to curtail in primarily gas homes.

## Pilot-Peak Time Rebate (hidden)
| Program Option: | Peak Time Rebate |  | Market PotentialWA | Market PotentialID |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes | Residential | #REF! | #REF!
|  |  |  | State | State |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  | Large General Service | #REF! | #REF!
| ParticipationRate | [5 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 0.19% |  | Modified for pilot scope | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 3.5 |  |  | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 2% |  | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: achieved 98% retention. Goal of 97% retention in next program cycle. | General Service | #REF! | #REF!
[7 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [5 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 0%
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential | 8.2% |  | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: 0.159 or 8.2% in summer, 0.134 or 7.1% in winter | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential | 0 |  |  | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential | 7.1% |  | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: 0.159 or 8.2% in summer, 0.134 or 7.1% in winter | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential | 0
| CEInput | [5 empty] | PGE Flex 2.0 PTR participation/EIA residential customer pop. est.
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | 898030.7805 |  |  | 2020 goal participation | 13.9% |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | - |  |  | 2020 participation | 11.69%
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | 29934.3594 |  |  | 2019 participation | 9.101% |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential | -
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 50 | [5 empty] | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 0 | [5 empty] | 50000
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | [5 empty] | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 0 |  | Assume zero, but would be $470 w tech costs included. Based on PacifiCorp estimate: $270 for PCT, plus $200 for installation |  |  |  | 1500000
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | [6 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 |  | If installed prior to Default AMI Rollout (indicated by Program Start Year), assume $177 cost for TOU meter ($162 from spreadsheet + $15 from email) [see Eli email 2/2/2016] |  |  |  | Residential | 59.87% | 29.71%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 40 |  | 4 hours per event, 15-20 events per year. 3 hours per event in PGE, 5 summer and 2 winter events. |  |  |  | General Service | 7.096% | 3.323%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 40 |  | 4 hours per event, 15-20 events per year. 3 hours per event in PGE, 5 summer and 2 winter events. |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential | 0 | [5 empty] | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 0 |  | Incentive built into rate design |  |  |  | Total | 66.97% | 33.03% | 100%
ResidentialProgram Life | Program Life | years | Residential | 10
ResidentialProgram Start Year | Program Start Year | year | Residential | 2024
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 0.19% |  | Modified for pilot scope
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 3.5 |  | Pacificorp. MISO used 1 year.
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1% |  | Consumer's DR Program
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 0%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service | 4.1% |  | Assumes half residential estimates from PGE Flex 2.0 PTR pilot evaliation 2021 | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 0 |  |  | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service | 3.55% |  | Assumes half residential estimates from PGE Flex 2.0 PTR pilot evaliation 2021 | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service | 0
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | 106444.278
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | 3548.1426
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | -
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 50
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 0
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 0 |  | Assume zero, but would be $470 w tech costs included. Based on PacifiCorp estimate: $270 for PCT, plus $200 for installation
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0 |  | If installed prior to Default AMI Rollout (indicated by Program Start Year), assume $220 for TOU meter ($245 from spreadsheet - $25 from email) [see Eli email 2/2/2016]
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 40 |  | 4 hours per event, 15-20 events per year
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | 40 |  | 4 hours per event, 15-20 events per year
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 0 |  | Incentive built into rate design
General ServiceProgram Life | Program Life | years | General Service | 10
General ServiceProgram Start Year | Program Start Year | year | General Service | 2024
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1

## Parent-Peak Time Rebate
| Program Option: | Peak Time Rebate |  | Market PotentialWA | Market PotentialID |  | Base Year Peak Usage per Customer (kW)
|  |  |  | Market Potential | Market Potential |  | WA | Summer | Winter
| Data Element | Unit | Customer Class | Market Potential | Market Potential | Notes | Residential | #REF! | #REF!
|  |  |  | State | State |  | General Service | #REF! | #REF!
|  |  |  | WA | ID |  | Large General Service | #REF! | #REF!
| ParticipationRate | [5 empty] | Extra Large General Service | #REF! | #REF!
ResidentialSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | Residential | 15% | 15% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: Goal of 110,000 out of ~800,000 residential customers (see table below) | ID
ResidentialProgram ramp up period | Program ramp up period | Years | Residential | 5 | 5 | Pacificorp. MISO used 1 year. | Residential | #REF! | #REF!
ResidentialProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | Residential | 2% | 2% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: achieved 98% retention. Goal of 97% retention in next program cycle. | General Service | #REF! | #REF!
[7 empty] | Large General Service | #REF! | #REF!
| ImpactInput | [5 empty] | Extra Large General Service | #REF! | #REF!
ResidentialEvent Non-Performance Rate | Event Non-Performance Rate | % | Residential | 0% | 0%
ResidentialPer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | Residential | 8.2% | 8.2% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: 0.159 or 8.2% in summer, 0.134 or 7.1% in winter | QC- impacts/customer | WA | ID
ResidentialPer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | Residential | 0 | 0 |  | Summer | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | Residential | 7.1% | 7.1% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: 0.159 or 8.2% in summer, 0.134 or 7.1% in winter | Winter | #REF! | #REF!
ResidentialPer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | Residential | 0 | 0
| CEInput | [5 empty] | PGE Flex 2.0 PTR participation/EIA residential customer pop. est.
ResidentialProgram Development Cost | Program Development Cost | $/program | Residential | 898030.7805 | 445675.5015 |  | 2020 goal participation | 13.9% |  | # FTEs per program- refer to Admin Costs and AssumptionsTab
ResidentialProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | Residential | - | - |  | 2020 participation | 11.69%
ResidentialAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | Residential | 29940.3462 | 14858.8212 |  | 2019 participation | 9.101% |  | Allocation based on share of 2042 (20-year) Summer MW potential
ResidentialAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | Residential | - | -
ResidentialPer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | Residential | 60 | 60 | 2024 Avista Update |  |  |  | Table to Allocate Program Admin Cost
ResidentialAnnual O&M Cost | Annual O&M Cost | $/participant/year | Residential | 0 | 0 |  |  |  |  | 50010 | 2024 Avista Update: + $10 for comminications
ResidentialAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | Residential | 0 | 0 |  |  |  |  | Table to Allocate Program Development Cost
ResidentialCost of Equip + Install | Cost of Equip + Install | $/tech | Residential | 0 | 0 | Assume zero, but would be $470 w tech costs included. Based on PacifiCorp estimate: $270 for PCT, plus $200 for installation |  |  |  | 1500000
ResidentialCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | Residential | 0 | 0 | [5 empty] | WA | ID
ResidentialAMI Cost | AMI Cost | $/program/year | Residential | 0 | 0 | If installed prior to Default AMI Rollout (indicated by Program Start Year), assume $177 cost for TOU meter ($162 from spreadsheet + $15 from email) [see Eli email 2/2/2016] |  |  |  | Residential | 59.87% | 29.71%
ResidentialSummer DR Event Hours | Summer DR Event Hours | hours/year | Residential | 40 | 40 | 4 hours per event, 15-20 events per year. 3 hours per event in PGE, 5 summer and 2 winter events. |  |  |  | General Service | 7.096% | 3.323%
ResidentialWinter DR Event Hours | Winter DR Event Hours | hours/year | Residential | 40 | 40 | 4 hours per event, 15-20 events per year. 3 hours per event in PGE, 5 summer and 2 winter events. |  |  |  | Large General Service | 0% | 0%
ResidentialPer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | Residential | 0 | 0 |  |  |  |  | Extra Large General Service | 0% | 0%
ResidentialPer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | Residential | 0.4 | 0.4 | 2024 Avista Update; per kWh reduced
ResidentialPer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | Residential | 0 | 0 | Incentive built into rate design |  |  |  | Total | 66.97% | 33.03% | 100%
ResidentialProgram Life | Program Life | years | Residential | 10 | 10
ResidentialProgram Start Year | Program Start Year | year | Residential | 2025 | 2028 | 2024 Avista: ID start in 2028
ResidentialDe-rate | De-rate | capacity equivalence factor | Residential | 1 | 1
ResidentialNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | Residential | 1 | 1
| Data Element | Unit | Customer Class | Market Potential | Market Potential
|  |  |  | State | State
|  |  |  | WA | ID
ParticipationRate
General ServiceSteady State Participation Rate | Steady State Participation Rate | % of eligible customers | General Service | 15% | 15% | PGE Res Pricing and Behavioral Pilot Flex PTR Evaluation 2021: Goal of 110,000 out of ~800,000 residential customers (see table below)
General ServiceProgram ramp up period | Program ramp up period | Years | General Service | 5 | 5 | Pacificorp. MISO used 1 year.
General ServiceProgram Dropout Rate (Attrition) | Program Dropout Rate (Attrition) | % of participating customers | General Service | 1% | 1% | Consumer's DR Program
ImpactInput
General ServiceEvent Non-Performance Rate | Event Non-Performance Rate | % | General Service | 0% | 0%
General ServicePer Customer Summer Peak Reduction (%) | Per Customer Summer Peak Reduction (%) | % of Peak | General Service | 4.1% | 4.1% | Assumes half residential estimates from PGE Flex 2.0 PTR pilot evaliation 2021 | QC- impacts/customer | WA | ID
General ServicePer Customer Summer Peak Reduction (kW) | Per Customer Summer Peak Reduction (kW) | kW @meter | General Service | 0 | 0 |  | Summer | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (%) | Per Customer Winter Peak Reduction (%) | % of Peak | General Service | 3.55% | 3.55% | Assumes half residential estimates from PGE Flex 2.0 PTR pilot evaliation 2021 | Winter | #REF! | #REF!
General ServicePer Customer Winter Peak Reduction (kW) | Per Customer Winter Peak Reduction (kW) | kW @meter | General Service | 0 | 0
CEInput
General ServiceProgram Development Cost | Program Development Cost | $/program | General Service | 106444.278 | 49849.4399
General ServiceProgram Development Cost (per MW basis) | Program Development Cost (per MW basis) | $/MW @meter | General Service | - | -
General ServiceAnnual Program Administration Cost | Annual Program Administration Cost | $/yr | General Service | 3548.8522 | 1661.9803
General ServiceAnnual Program Administration Cost (per MW basis) | Annual Program Administration Cost (per MW basis) | $/MW @meter | General Service | - | -
General ServicePer Customer Annual Marketing/Recruitment Cost | Per Customer Annual Marketing/Recruitment Cost | $/new participant/year | General Service | 60 | 60 | 2024 Avista Update
General ServiceAnnual O&M Cost | Annual O&M Cost | $/participant/year | General Service | 0 | 0
General ServiceAnnual O&M Cost per MW | Annual O&M Cost per MW | $/MW @meter | General Service | 0 | 0
General ServiceCost of Equip + Install | Cost of Equip + Install | $/tech | General Service | 0 | 0 | Assume zero, but would be $470 w tech costs included. Based on PacifiCorp estimate: $270 for PCT, plus $200 for installation
General ServiceCost of Equip + Install (per kW basis) | Cost of Equip + Install (per kW basis) | $/kW @meter | General Service | 0 | 0
General ServiceAMI Cost | AMI Cost | $/program/year | General Service | 0 | 0 | If installed prior to Default AMI Rollout (indicated by Program Start Year), assume $220 for TOU meter ($245 from spreadsheet - $25 from email) [see Eli email 2/2/2016]
General ServiceSummer DR Event Hours | Summer DR Event Hours | hours/year | General Service | 40 | 40 | 4 hours per event, 15-20 events per year
General ServiceWinter DR Event Hours | Winter DR Event Hours | hours/year | General Service | 40 | 40 | 4 hours per event, 15-20 events per year
General ServicePer kW Annual Incentive | Per kW Annual Incentive | $/kW @meter/year | General Service | 0 | 0
General ServicePer kWh Annual Incentive | Per kWh Annual Incentive | $/kWh @meter | General Service | 0.4 | 0.4 | 2024 Avista Update; per kWh reduced
General ServicePer Participant Annual Incentive | Per Participant Annual Incentive | $/participant/year | General Service | 0 | 0 | Incentive built into rate design
General ServiceProgram Life | Program Life | years | General Service | 10 | 10
General ServiceProgram Start Year | Program Start Year | year | General Service | 2025 | 2028 | 2024 Avista: ID start in 2028
General ServiceDe-rate | De-rate | capacity equivalence factor | General Service | 1 | 1
General ServiceNet to Gross Ratio (free ridership) | Net to Gross Ratio (free ridership) | ratio | General Service | 1 | 1
Note on O26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Removed Development costs from parent program. Modeling up-front costs in the pilot Reply: For "Considered" program scenario, all costs stay in parents. No pilots.

## Admin Costs and Asmptns.
# FTEs * Revised
| Number of Full-Time Employees (FTEs) | 8
| Number of Programs | 16
| FTE Cost | 150000
| Total FTE Cost | 1200000
| Cost / Program | 75000
| Base Development Cost | 75000
| Total Development Cost | 1200000
|  | Admin Allocator | Total Admin Cost | Development Cost | # FTE's
| DLC Central AC | 0.075 | 90000 | 75000 | 3
| DLC Water Heating | 0.075 | 90000 | 75000
| CTA-2045 | 0.075 | 90000 | 75000
2024 Avista Update | DLC Smart Thermostats - Cooling | 0.075 | 90000 | 250000
| DLC Smart Appliances | 0.075 | 90000 | 75000
2024 Avista Update | Time-of-use Rates | 0.083333 | 100000 | 1000000 | 2
| Electric Vehicle TOU Opt-in | 0.0625 | 75000 | 0
| Variable Peak Pricing Rates | 0.0625 | 75000 | 75000
2024 Avista Update | Peak Time Rebate | 0.041667 | 50000 | 1500000
| Thermal Energy Storage | 0.05 | 60000 | 75000 | 2
| Battery Energy Storage | 0.05 | 60000 | 75000
| DLC Electric Vehicle Charging | 0.05 | 60000 | 200000
| Behavioral | 0.05 | 60000 | 100000
| Ancillary Services | 0.05 | 60000 | 75000
| Third Party Contracts | 0.125 | 150000 | 75000 | 1
| Total | 1 | 1200000 | 3725000
Old | Time-of-use Rates | 0.0625 | 75000 | 75000
Old | Peak Time Rebate | 0.0625 | 75000 | 75000
Old | DLC Smart Thermostats - Cooling | 0.075 | 90000 | 75000
% Share of Seasonal 20-year potential by program
|  | WA | WA | WA | WA | ID | ID | ID | ID
| Option | Extra Large General Service | General Service | Large General Service | Residential | Extra Large General Service | General Service | Large General Service | Residential | Notes
| Ancillary Battery Storage | 0.03121% | 5.627% | 2.577% | 55.87% | 0.01635% | 4.208% | 1.218% | 30.46% | Share of 20 year Summer potential
| Ancillary Cooling | 0% | 5.521% | 0% | 57.73% | 0% | 3.487% | 0% | 33.27% | Share of 20 year Summer potential
| Ancillary DLC WH | 0% | 0% | 0% | 0% | 0% | 9.707% | 0% | 90.29% | Share of 20 year Summer potential
| Parent-Ancillary HPWH | 0% | 78.93% | 0% | 21.07% | 0% | 0% | 0% | 0% | Share of 20 year Summer potential
| Parent-Ancillary ERWH | 0% | 9.144% | 0% | 90.86% | 0% | 0% | 0% | 0% | Share of 20 year Summer potential
| Ancillary EV | 0% | 0% | 0% | 53.39% | 0% | 0% | 0% | 46.61% | Share of 20 year Summer potential
| Ancillary Heating | 0% | 2.316% | 0% | 61.41% | 0% | 1.648% | 0% | 34.62% | Share of 20 year Winter potential
| Ancillary Third Party | 14.69% | 9.65% | 49.19% | 0% | 7.499% | 3.567% | 15.41% | 0% | Share of 20 year Summer potential
| Battery Energy Storage | 0.03121% | 5.627% | 2.577% | 55.87% | 0.01635% | 4.208% | 1.218% | 30.46% | Share of 20 year Summer potential
| Behavioral | 0% | 0% | 0% | 66.83% | 0% | 0% | 0% | 33.17% | Share of 20 year Summer potential
| DLC Central AC | 0% | 5.521% | 0% | 57.73% | 0% | 3.487% | 0% | 33.27% | Share of 20 year Summer potential
| DLC Electric Vehicle Charging | 0% | 0% | 0% | 53.39% | 0% | 0% | 0% | 46.61% | Share of 20 year Summer potential
| DLC Smart Appliances | 0% | 5.851% | 0% | 58.1% | 0% | 4.377% | 0% | 31.67% | Share of 20 year Summer potential
| DLC Smart Thermostats - Cooling | 0% | 5.521% | 0% | 57.73% | 0% | 3.487% | 0% | 33.27% | Share of 20 year Summer potential
| DLC Smart Thermostats - Heating | 0% | 2.316% | 0% | 61.41% | 0% | 1.648% | 0% | 34.62% | Share of 20 year Winter potential
| DLC Water Heating | 0% | 0% | 0% | 0% | 0% | 9.707% | 0% | 90.29% | Share of 20 year Summer potential
| CTA-2045 HPWH | 0% | 78.93% | 0% | 21.07% | 0% | 0% | 0% | 0% | Share of 20 year Summer potential
| CTA-2045 ERWH | 0% | 9.144% | 0% | 90.86% | 0% | 0% | 0% | 0% | Share of 20 year Summer potential
| Electric Vehicle TOU Opt-in | 0% | 6.471% | 93.53% | 0% | 0% | 0% | 0% | 0% | Share of 20 year Summer potential
| Thermal Energy Storage | 0.3563% | 32.12% | 29.42% | 0% | 0.1866% | 24.02% | 13.9% | 0% | Share of 20 year Summer potential
| Third Party Contracts | 13.72% | 9.013% | 45.94% | 0% | 8.874% | 4.221% | 18.23% | 0% | Share of 20 year Summer potential
2024 Avista Update | Time-of-Use Opt-Out | 0% | 19.78% | 0% | 47.47% | 0% | 9.202% | 0% | 23.56% | Share of 20 year Summer potential
| Variable Peak Pricing Rates | 16.35% | 0% | 52.31% | 0% | 10.58% | 0% | 20.76% | 0% | Share of 20 year Summer potential
2024 Avista Update | Time-of-Use Opt-in | 0% | 13.36% | 0% | 53.75% | 0% | 6.216% | 0% | 26.68% | Share of 20 year Summer potential
| Peak Time Rebate | 0% | 7.096% | 0% | 59.87% | 0% | 3.323% | 0% | 29.71% | Share of 20 year Summer potential
Old | Time-of-Use Opt-Out | 5.23% | 0.6552% | 13.89% | 47.47% | 3.383% | 0.3068% | 5.512% | 23.56% | Share of 20 year Summer potential
Old | Time-of-Use Opt-in | 3.533% | 0.4426% | 9.382% | 53.75% | 2.285% | 0.2073% | 3.723% | 26.68% | Share of 20 year Summer potential
Note on B16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: These costs are applied to each CTA program.
Note on B17: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sharing admin/dev costs with heating on the program tab. No costs associated with heating program.
Note on B19: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: These costs are applied to each TOU rate. Only one TOU rate (opt-in or opt-out) can be offered at a time.
Note on B27: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: These costs are applied to each ancillary program.
Note on B32: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: These costs are applied to each TOU rate. Only one TOU rate (opt-in or opt-out) can be offered at a time.
Note on B34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Sharing admin/dev costs with heating on the program tab. No costs associated with heating program.
Admin Costs
1. estimate # of FTEs look at average cost / program.
Allocate to programs based on size with some minimum amount for each program
Development costs
150,000 as a baseline then increase and decrease based on program
Marketing costs
based on class and program
O&M based on program
5% of equipment cost - exception include storage ancillary and voltage
Equipment
program specific / benchmarked
Incentive
program specific / benchmarked

## CTs + Demand - To be updated
Winter Peak
| Washington | [7 empty] | Previous CPA Control Totals
| Sector | Energy (GWh) | Load Factor (W) | Demand (W) | Calibrated Demand (W) |  | Energy % | (W) Demand % | Sector | Energy (GWh) | Load Factor (W) | Demand (W) | Calibrated Demand (W) |  | Energy % | (W) Demand %
| Residential | 2696.3538 | 0.6131 | 502.0448 | 502.0448 |  | 51.04% | 50.45% | Residential | 2539.1736 | 0.63 | 460.0952 | 472.7788 |  | 44.89% | 44.59%
| Commercial | 2041.7893 | 0.5839 | 399.1773 | 399.1773 |  | 38.65% | 40.11% | Commercial | 2165.9975 | 0.6 | 412.1 | 423.4604 |  | 38.29% | 39.94%
| Industrial | 544.6824 | 0.66176 | 93.9595 | 93.9595 |  | 10.31% | 9.441% | Industrial | 951.1316 | 0.68 | 159.6716 | 164.0733 |  | 16.82% | 15.47%
| WA Total | 5282.8255 |  | 995.1815 | 995.1815 |  |  |  | WA Total | 5656.3027 |  | 1031.8668 | 1060.3125
Idaho
| Sector | Energy (GWh) | Load Factor (W) | Demand (W) | Calibrated Demand (W) |  | Energy % | (W) Demand % | Sector | Energy (GWh) | Load Factor (W) | Demand (W) | Calibrated Demand (W) |  | Energy % | (W) Demand %
| Residential | 1325.0617 | 0.63256 | 239.1271 | 239.1271 |  | 48.69% | 48.35% | Residential | 1235.7519 | 0.65 | 217.027 | 223.0099 |  | 47.74% | 47.49%
| Commercial | 982.8077 | 0.64229 | 174.675 | 174.675 |  | 36.12% | 35.32% | Commercial | 1007.2811 | 0.66 | 174.2219 | 179.0247 |  | 38.91% | 38.12%
| Industrial | 413.3044 | 0.5839 | 80.8025 | 80.8025 |  | 15.19% | 16.34% | Industrial | 345.6354 | 0.6 | 65.7602 | 67.573 |  | 13.35% | 14.39%
| ID Total | 2721.1737 |  | 494.6047 | 494.6047 |  |  |  | ID Total | 2588.6683 |  | 457.009 | 469.6075
| Avista Total | 8003.9993 |  | 1489.7862 | 1489.7862 |  |  |  | Avista Total | 8244.971 |  | 1488.8758 | 1529.92
|  |  |  | Control Total | 1050.5417 | 2021-02-01 | Load less CWTR and Inland Paper (consistent with industrial kWh) |  |  |  |  | Control Total | 1529.92 | 2019-02-01 | Load less CWTR (consistent with industrial kWh)
[5 empty] | Not using monthly aMW above. We were not provided peak data in the same format as the previous study. | [8 empty] | New SAS Monthly Peak Load Data.xlsx
Summer Peak
| Washington | [7 empty] | Previous CPA Control Totals
| Sector | Energy (GWh) | Load Factor (S) | Demand (S) | Calibrated Demand (S) |  | Energy % | (S) Demand % | Sector | Energy (GWh) | Load Factor (S) | Demand (S) | Calibrated Demand (S) |  | Energy % | (S) Demand %
| Residential | 2696.3538 | 0.56944 | 540.5343 | 540.5343 |  | 51.04% | 52.69% | Residential | 2539.1736 | 0.5 | 579.72 | 509.0246 |  | 44.89% | 47.07%
| Commercial | 2041.7893 | 0.58083 | 401.2889 | 401.2889 |  | 38.65% | 39.12% | Commercial | 2165.9975 | 0.51 | 484.8235 | 425.7005 |  | 38.29% | 39.37%
| Industrial | 544.6824 | 0.74027 | 83.9936 | 83.9936 |  | 10.31% | 8.188% | Industrial | 951.1316 | 0.65 | 167.041 | 146.6708 |  | 16.82% | 13.56%
| WA Total | 5282.8255 |  | 1025.8168 | 1025.8168 |  |  |  | WA Total | 5656.3027 |  | 1231.5845 | 1081.3959
| Idaho | [7 empty] | Sector | Energy (GWh) | Load Factor (S) | Demand (S) | Calibrated Demand (S) |  | Energy % | (S) Demand %
| Sector | Energy (GWh) | Load Factor (S) | Demand (S) | Calibrated Demand (S) |  | Energy % | (S) Demand % | Residential | 1235.7519 | 0.53 | 266.1652 | 233.707 |  | 47.74% | 49.08%
| Residential | 1325.0617 | 0.60361 | 250.5974 | 250.5974 |  | 48.69% | 49.96% | Commercial | 1007.2811 | 0.57 | 201.7306 | 177.13 |  | 38.91% | 37.2%
| Commercial | 982.8077 | 0.64916 | 172.8264 | 172.8264 |  | 36.12% | 34.46% | Industrial | 345.6354 | 0.53 | 74.4455 | 65.367 |  | 13.35% | 13.73%
| Industrial | 413.3044 | 0.60361 | 78.1647 | 78.1647 |  | 15.19% | 15.58%
[9 empty] | ID Total | 2588.6683 |  | 542.3412 | 476.2041
| ID Total | 2721.1737 |  | 501.5885 | 501.5885
[9 empty] | Avista Total | 8244.971 |  | 1773.9258 | 1557.6
| Avista Total | 8003.9993 |  | 1527.4053 | 1527.4053
[12 empty] | Control Total | 1557.6 | 2019-08-01 | Load less CWTR (consistent with industrial kWh)
|  |  |  | Control Total | 997.3313 | 2021-07-01 | Load less CWTR and Inland Paper (consistent with industrial kWh) | [6 empty] | New SAS Monthly Peak Load Data.xlsx
Not using monthly aMW above. We were not provided peak data in the same format as the previous study.
Notes:
-Currently including Com schedules 13 and 23 for general service vehicle charging and large general service vehicle charging. Keep these? --> Yes
-Currently keeping "Schedule 31- pumping service" from C&I. Keep these? --> moved commercial pumping into industrial
Note on D4: Fuong Nguyen: KEMA System Load Research Project ID Tables- 29, 32, 35 WA Tables- 14, 17, 20 KK: added "Pumping" from tables 25 and 41 Source: \\EgnyteDrive\Ameresco Files\AEG\Clients\Avista Energy\1341 Avista CPA\X_2010 CPA\Utility provided data and Background documents\Load Research Report 2009 KEMA\2009 COS Report V01_3-15-10 KEMA jb annotations.doc
Note on N4: Fuong Nguyen: KEMA System Load Research Project, Tables 29, 32, 35 KK: added "Pumping" from tables 25 and 41
Note on D26: Fuong Nguyen: KEMA System Load Research Project ID Tables- 29, 32, 35 WA Tables- 14, 17, 20 KK: added "Pumping" from tables 25 and 41 Source: \\EgnyteDrive\Ameresco Files\AEG\Clients\Avista Energy\1341 Avista CPA\X_2010 CPA\Utility provided data and Background documents\Load Research Report 2009 KEMA\2009 COS Report V01_3-15-10 KEMA jb annotations.doc
Note on N26: Fuong Nguyen: KEMA System Load Research Project, Tables 29, 32, 35 KK: added "Pumping" from tables 25 and 41

## DR- Forecasts
| Source: Electricity Data and Forecasts Spring 2024v2, "Spring 2024 Forecasts" tab | [11 empty] | Source: Electricity Data and Forecasts Spring 2024v2, "Spring 2024 Forecasts" tab
| Updated 4/17/2024 | [11 empty] | Updated 4/17/2024
| Commercial Schedules, Washington | [6 empty] | General Service Vehicle Charging |  | Large General Service Vehicle Charging |  |  | Commerical Schedules, Idaho
|  | WASCH11CUS.c | WASCH11KWH.c | WASCH21CUS.c | WASCH21KWH.c | WASCH25CUS.c | WASCH25KWH.c | WASCH13CUS.c | WASCH13KWH.c | WASCH23CUS.c | WASCH23KWH.c |  |  | IDSCH11CUS.c | IDSCH11KWH.c | IDSCH21CUS.c | IDSCH21KWH.c | IDSCH25CUS.c | IDSCH25KWH.c
| 2023-03-01 | 23870.5 | 55146083.5098 | 1566 | 96261910.2894 | 10 | 23410101.801 | 9 | 21604.95 | 6 | 141125.36 |  | 2023-03-01 | 17505 | 40349780.5656 | 656.5 | 41230373.2353 | 3 | 2790503.809
| 2023-04-01 | 24352.5 | 49060440.3286 | 1596 | 90054977.6322 | 10 | 22115950.64 | 8 | 26094.16 | 2 | 21888.12 |  | 2023-04-01 | 17527 | 35592377.4649 | 640.5 | 38667009.8141 | 3 | 4612489
| 2023-05-01 | 24352.5 | 45040289.8491 | 1596 | 92540703.6485 | 10 | 23846640.16 | 9 | 26715.35 | 4 | 78707.48 |  | 2023-05-01 | 17527 | 33112611.7183 | 640.5 | 37602015.3377 | 3 | 4902221.8
| 2023-06-01 | 24015 | 45973035.492 | 1587 | 97078887.357 | 10 | 23825765.7 | 14 | 31392.35 | 3 | 38407.84 |  | 2023-06-01 | 17663 | 34510693.028 | 634 | 40208929.6 | 3 | 4834789.4
| 2023-07-01 | 23905 | 50763510.64 | 1569 | 101075324.298 | 10 | 26158420.27 | 11 | 47335.68 | 3 | 88914.88 |  | 2023-07-01 | 17567 | 37921266.757 | 610 | 41396453.8 | 3 | 5418396.2
| 2023-08-01 | 24062 | 55220439.041 | 1573 | 106529586.019 | 10 | 26532611.76 | 11 | 54175.16 | 3 | 110835.56 |  | 2023-08-01 | 17689 | 41442877.899 | 586 | 42502852 | 3 | 5547908.8
| 2023-09-01 | 24012 | 49085557.036 | 1551 | 99408459.272 | 10 | 23772083.059 | 11 | 44451.83 | 3 | 120333.36 |  | 2023-09-01 | 17675 | 38752894.7549 | 525 | 38757988.4 | 3 | 5039249.6
| 2023-10-01 | 24111 | 43565099.765 | 1572 | 92230516.05 | 10 | 23465827.6 | 14 | 56794.56 | 3 | 149251.92 |  | 2023-10-01 | 17886 | 34865417.4173 | 478 | 33856136.04 | 3 | 5053288.8
| 2023-11-01 | 24013 | 48101688.56 | 1559 | 94016660.625 | 10 | 22399531.81 | 13 | 50028.14 | 3 | 184096.12 |  | 2023-11-01 | 17793 | 39704022.676 | 445 | 33944606.6 | 3 | 4522117.6
| 2023-12-01 | 24026.5 | 56812232.1849 | 1561.5 | 101298124.2709 | 10 | 22720054.761 | 18 | 53472.7 | 1 | 28864.8 |  | 2023-12-01 | 17850.5 | 47450565.9331 | 414 | 35221823.0693 | 3 | 4537912.4
| 2024-01-01 | 24040 | 61171945.1954 | 1564 | 105724296.398 | 10 | 23881118.32 | 20 | 53399.27 | 3 | 223934.56 |  | 2024-01-01 | 17908 | 54144083.246 | 383 | 37101563.4 | 3 | 4766787.2
| 2024-02-01 | 24202 | 57769288.097 | 1569 | 98475761.202 | 10 | 22094442.23 | 25 | 52625.12 | 3 | 323828.88 |  | 2024-02-01 | 18024 | 52534424.016 | 353 | 33749349.8 | 3 | 4443804.4
| 2076.6274 | [11 empty] | 1001.0896
| Source: Electricity Data and Forecasts Spring 2024v2, "Spring 2024 Forecasts" tab | [11 empty] | Source: Electricity Data and Forecasts Spring 2024v2, "Spring 2024 Forecasts" tab
| Updated 4/17/2024 | [11 empty] | Updated 4/17/2024
| Industrial Schedules, Washington |  |  | Without Inland Paper |  |  | Without Inland Paper | [5 empty] | Industrial Schedules, Idaho, Excludes Clearwater Paper (Potlatch, Schedule 25P)
|  | WASCH11CUS.i | WASCH11KWH.i | WASCH21CUS.i | WASCH21KWH.i | WASCH25CUS.i.NOINLAND | WASCH25KWH.i.NOINLAND | [6 empty] | IDSCH11CUS.i | IDSCH11KWH.i | IDSCH21CUS.i | IDSCH21KWH.i | IDSCH25CUS.i | IDSCH25KWH.i
| 2023-03-01 | 98 | 479844.895 | 67 | 7620197.6403 | 11 | 29358997.107 | [5 empty] | 2023-03-01 | 116 | 591023.8994 | 44.5 | 4916563.9583 | 8 | 24959265.72
| 2023-04-01 | 101.5 | 451087.0666 | 71.5 | 8153065.7288 | 11 | 28212850.2 | [5 empty] | 2023-04-01 | 116 | 501054.4972 | 44 | 5507898.5366 | 8 | 23419545.6
| 2023-05-01 | 101.5 | 348637.6642 | 71.5 | 6687106.8027 | 11 | 27601398.1 | [5 empty] | 2023-05-01 | 116 | 469979.2719 | 44 | 4821922.5532 | 8 | 23315330.64
| 2023-06-01 | 98 | 322954.021 | 68 | 7061996.71 | 11 | 28988726.2 | [5 empty] | 2023-06-01 | 116 | 412368.61 | 44 | 5213367.9 | 8 | 23776263.16
| 2023-07-01 | 98 | 331430.386 | 67 | 7211161.38 | 11 | 26337626.9 | [5 empty] | 2023-07-01 | 117 | 449918.97 | 43 | 5232379 | 8 | 23115779.04
| 2023-08-01 | 97 | 359012.863 | 69 | 7660634.97 | 11 | 30422711.7 | [5 empty] | 2023-08-01 | 116 | 578063.19 | 42 | 5104391 | 8 | 22157940.799
| 2023-09-01 | 98 | 346352.873 | 68 | 7150690.35 | 11 | 29504207.798 | [5 empty] | 2023-09-01 | 118 | 512421.08 | 39 | 4669603 | 8 | 19829310.32
| 2023-10-01 | 98 | 322217.336 | 68 | 6803054.03 | 11 | 29653320.35 | [5 empty] | 2023-10-01 | 119 | 563633.46 | 38 | 4706066 | 8 | 23266394.3
| 2023-11-01 | 96 | 391913.754 | 68 | 7086490.75 | 11 | 28058870.2 | [5 empty] | 2023-11-01 | 118 | 594219.85 | 38 | 4861022 | 8 | 21995648.51
| 2023-12-01 | 96 | 490044.549 | 68 | 8120132.7593 | 11 | 25926966.7 | [5 empty] | 2023-12-01 | 118 | 672954.383 | 35 | 5498138.3333 | 8 | 21973829.49
| 2024-01-01 | 96 | 532738.225 | 68 | 7898521.31 | 11 | 29468325.3 | [5 empty] | 2024-01-01 | 122 | 801581.25 | 32 | 5346325 | 8 | 24557888.27
| 2024-02-01 | 96 | 679223.362 | 66 | 7592379.9 | 11 | 29226224.4 | [5 empty] | 2024-02-01 | 123 | 774182.53 | 32 | 5085683 | 8 | 24300945.9
| 436.8611 | [11 empty] | 344.5529
| Source: Electricity Data and Forecasts Spring 2024v2, "Spring 2024 Forecasts" tab | [11 empty] | Source: Electricity Data and Forecasts Spring 2024v2, "Spring 2024 Forecasts" tab
| Updated 4/17/2024 | [11 empty] | Updated 4/17/2024
| Current Forecast Date: Fall 2021 |  |  |  | General Service Vehicle Charging | Large General Service Vehicle Charging |  |  |  | General Service Vehicle Charging | Large General Service Vehicle Charging |  | Current Forecast Date: Fall 2021
| Year | WASCH11CUS.c | WASCH21CUS.c | WASCH25CUS.c | WASCH13CUS.c | WASCH23CUS.c | WASCH11KWH.c | WASCH21KWH.c | WASCH25KWH.c | WASCH13KWH.c | WASCH23KWH.c |  |  | IDSCH11CUS.c | IDSCH21CUS.c | IDSCH25CUS.c | IDSCH11KWH.c | IDSCH21KWH.c | IDSCH25KWH.c
2019 | 2019 Actual | 22713.5417 | 1772.25 | 10 | 0 | 0 | 557344513.3862 | 1242992567.8321 | 289294535.741 | 0 | 0 |  | 2019 Actual | 16220.4583 | 981.0833 | 3 | 355231954.2927 | 555061867.2 | 62388727.0227 | 565764.2408
2020 | 2020 Actual | 23048.75 | 1751.4167 | 10 | 0 | 0 | 527691988.3501 | 1148654645.3131 | 269999572.979 | 0 | 0 |  | 2020 Actual | 16524.1667 | 878.5 | 3 | 363872150.745 | 511154280.03 | 60263968.1 | 581848.9243
2021 | 2021 Actual | 23421.5833 | 1673.4167 | 10 | 2.7143 | 2.875 | 580916093.3995 | 1190145022.0412 | 279253091.768 | 38901.37 | 87569.75 |  | 2021 Actual | 16848.4167 | 790.9167 | 3 | 399763959.9423 | 511727664.9189 | 63232142.6037 | 647005.7928
2022 | 2022 Actual | 23765.1667 | 1590.375 | 10 | 4.9167 | 2.9167 | 612468857.47 | 1196634299.2936 | 285594158.506 | 189126.39 | 247554.31 |  | 2022 Actual | 17165.3333 | 710.6667 | 3 | 429904049.9639 | 504797085.2332 | 61039672.883 | 710314.8479
2023 | 2023 Actual | 24051.4583 | 1572.2083 | 10 | 11.0833 | 2.9167 | 617908656.5631 | 1175301966.133 | 283828835.191 | 445047.02 | 1016251.47 |  | 2023 Actual | 17598.4167 | 631.8056 | 3 | 457007895.4289 | 494888605.3097 | 55616767.009 | 783292.5826
2024 | 2024 Forecast | 24284.9167 | 1559.625 | 10 | 17.6535 | 2.789 | 609924604.2924 | 1159462137.35 | 284952440.55 | 602987.3769 | 2447813.9595 |  | 2024 Forecast | 17867 | 608.9167 | 3 | 452091539 | 489440756.4167 | 60013017 | 803789.3906
2025 | 2025 Forecast | 24530.5833 | 1547.25 | 10 | 17.1312 | 2.7279 | 608524515 | 1144925154 | 286093360 | 602642.6514 | 2315283.029 |  | 2025 Forecast | 18134.5 | 584.9167 | 3 | 459010708 | 483085698 | 60169344 | 825905.1683
2026 | 2026 Forecast | 24743.9167 | 1535.25 | 10 | 17.1574 | 2.727 | 613786983 | 1128682539 | 287014030 | 603576.8977 | 2313167.5732 |  | 2026 Forecast | 18401.9167 | 560.9167 | 3 | 464497593 | 475916883.8333 | 60602688 | 848462.7256
2027 | 2027 Forecast | 24958.0833 | 1523.25 | 10 | 17.1554 | 2.7273 | 619071629 | 1108218345.25 | 287562790 | 603499.7491 | 2313450.0169 |  | 2027 Forecast | 18671.5833 | 536.9167 | 3 | 471064584 | 467722025.0833 | 60877626 | 871125.9198
2028 | 2028 Forecast | 25187.3333 | 1511.25 | 10 | 17.1556 | 2.7273 | 624768066 | 1084863901.75 | 287967900 | 603505.4499 | 2313432.4095 |  | 2028 Forecast | 18941.4167 | 512.9167 | 3 | 477514084 | 458446145.25 | 61153890 | 893802.3953
2020 | 2020 Actual | 1.476% | -1.176% | 0% | 0% | 0% | -5.32% | -7.59% | -6.67% | 0% | 0% |  | 2018 Actual | 1.872% | -10.46% | 0% | 2.432% | -7.91% | -3.406%
2021 | 2021 Actual | 1.618% | -4.454% | 0% | 0% | 0% | 10.09% | 3.612% | 3.427% | 0% | 0% |  | 2019 Actual | 1.962% | -9.97% | 0% | 9.864% | 0.1122% | 4.925%
2022 | 2022 Actual | 1.467% | -4.962% | 0% | 81.14% | 1.449% | 5.432% | 0.5453% | 2.271% | 386.2% | 182.7% |  | 2020 Actual | 1.881% | -10.15% | 0% | 7.539% | -1.354% | -3.467%
2023 | 2023 Actual | 1.205% | -1.142% | 0% | 125.4% | 0% | 0.8882% | -1.783% | -0.6181% | 135.3% | 310.5% |  | 2021 Forecast | 2.523% | -11.1% | 0% | 6.305% | -1.963% | -8.884%
2024 | 2024 Forecast | 0.9707% | -0.8004% | 0% | 59.28% | -4.376% | -1.292% | -1.348% | 0.3959% | 35.49% | 140.9% |  | 2022 Forecast | 1.526% | -3.623% | 0% | -1.076% | -1.101% | 7.905%
2025 | 2025 Forecast | 1.012% | -0.7935% | 0% | -2.958% | -2.191% | -0.2296% | -1.254% | 0.4004% | -0.05717% | -5.414% |  | 2023 Forecast | 1.497% | -3.941% | 0% | 1.53% | -1.298% | 0.2605%
2026 | 2026 Forecast | 0.8697% | -0.7756% | 0% | 0.153% | -0.03375% | 0.8648% | -1.419% | 0.3218% | 0.155% | -0.09137% |  | 2024 Forecast | 1.475% | -4.103% | 0% | 1.195% | -1.484% | 0.7202%
2027 | 2027 Forecast | 0.8655% | -0.7816% | 0% | -0.01178% | 0.01133% | 0.861% | -1.813% | 0.1912% | -0.01278% | 0.01221% |  | 2025 Forecast | 1.465% | -4.279% | 0% | 1.414% | -1.722% | 0.4537%
2028 | 2028 Forecast | 0.9185% | -0.7878% | 0% | 0.0009569% | -0.000796% | 0.9202% | -2.107% | 0.1409% | 0.0009446% | -0.0007611% |  | 2026 Forecast | 1.445% | -4.47% | 0% | 1.369% | -1.983% | 0.4538%
| Avg. Annual Growth | 0.9687% | -0.8505% | 0% | 20.83% | -1.119% | 0.3314% | -1.634% | 0.138% | 19.34% | 37.25% |  | Avg. Annual Growth | 1.641% | -5.435% | 0% | 1.751% | -1.605% | 0.03116%
| Year | WASCH11CUS.i | WASCH21CUS.i | WASCH25CUS.i (Excluding IEP) | WASCH11KWH.i | WASCH21KWH.i | WASCH25KWH.i (Excluding IEP) | [5 empty] | Year | IDSCH11CUS.i | IDSCH21CUS.i | IDSCH25CUS.i | IDSCH11KWH.i | IDSCH21KWH.i | IDSCH25KWH.i
2019 | 2019 Actual | 125.0833 | 75.5833 | 12 | 6099069.73 | 91124146.15 | 341448188.9893 | [5 empty] | 2019 Actual | 121.3333 | 57.4167 | 7.4167 | 5346402.52 | 66077310 | 249292120.4247
2020 | 2020 Actual | 118.3333 | 71.3333 | 12 | 5842118.444 | 85559821.3 | 293266572.971 | [5 empty] | 2020 Actual | 119.5417 | 54.4167 | 8.0833 | 5057573.2098 | 60018739.6 | 270693164.607
2021 | 2021 Actual | 96.5 | 70.4167 | 11.4167 | 5292386.4616 | 91492005.9801 | 303454290.8877 | [5 empty] | 2021 Actual | 114.5 | 46.5833 | 8 | 5478416.0733 | 59284937.137 | 281585393.3203
2022 | 2022 Actual | 97.9167 | 67.6667 | 11 | 5097825.1198 | 94578563.858 | 337897395.449 | [5 empty] | 2022 Actual | 115.8333 | 45.25 | 8 | 5889201.6449 | 57616569.2291 | 290907205.873
2023 | 2023 Actual | 98.4167 | 68.5 | 11 | 5056586.13 | 89533210.6401 | 342893243.155 | [5 empty] | 2023 Actual | 116.75 | 41.5833 | 8 | 6178529.5983 | 60860335.5709 | 283599257.869
2024 | 2024 Forecast | 97.0268 | 66.9556 | 11 | 5085425.8257 | 89323870.4367 | 339923222.7 | [5 empty] | 2024 Forecast | 119.6139 | 34.2306 | 8 | 5999365.8833 | 55147090.0084 | 287343343
2025 | 2025 Forecast | 97.0819 | 65.1867 | 11 | 4862651.146 | 86858927.2267 | 333173665 | [5 empty] | 2025 Forecast | 117.4967 | 32.2567 | 8 | 6038872.7833 | 52442748.7891 | 287287315
2026 | 2026 Forecast | 97.0729 | 63.2667 | 11 | 4862041.9462 | 84289405.2667 | 329558911 | [5 empty] | 2026 Forecast | 115.8167 | 29.6167 | 8 | 6041058.85 | 50480553.4108 | 287249487
2027 | 2027 Forecast | 97.0707 | 61.3467 | 11 | 4861888.571 | 81724920.92 | 327403571 | [5 empty] | 2027 Forecast | 114.1367 | 26.9767 | 8 | 6062466.0167 | 47249927.603 | 287244461
2028 | 2028 Forecast | 97.0705 | 59.4267 | 11 | 4861873.1859 | 79156090.44 | 326149846 | [5 empty] | 2028 Forecast | 112.4567 | 24.3367 | 8 | 6068606.8333 | 44548082.5218 | 287246960
2020 | 2018 Actual | -5.396% | -5.623% | 0% | -4.213% | -6.106% | -14.11% | [5 empty] | 2018 Actual | -1.477% | -5.225% | 8.989% | -5.402% | -9.169% | 8.585%
2021 | 2019 Actual | -18.45% | -1.285% | -4.861% | -9.41% | 6.933% | 3.474% | [5 empty] | 2019 Actual | -4.217% | -14.4% | -1.031% | 8.321% | -1.223% | 4.024%
2022 | 2020 Actual | 1.468% | -3.905% | -3.65% | -3.676% | 3.374% | 11.35% | [5 empty] | 2020 Actual | 1.164% | -2.862% | 0% | 7.498% | -2.814% | 3.31%
2023 | 2021 Forecast | 0.5106% | 1.232% | 0% | -0.809% | -5.335% | 1.479% | [5 empty] | 2021 Forecast | 0.7914% | -8.103% | 0% | 4.913% | 5.63% | -2.512%
2024 | 2022 Forecast | -1.412% | -2.255% | 0% | 0.5703% | -0.2338% | -0.8662% | [5 empty] | 2022 Forecast | 2.453% | -17.68% | 0% | -2.9% | -9.387% | 1.32%
2025 | 2023 Forecast | 0.05679% | -2.642% | 0% | -4.381% | -2.76% | -1.986% | [5 empty] | 2023 Forecast | -1.77% | -5.766% | 0% | 0.6585% | -4.904% | -0.0195%
2026 | 2024 Forecast | -0.009309% | -2.945% | 0% | -0.01253% | -2.958% | -1.085% | [5 empty] | 2024 Forecast | -1.43% | -8.184% | 0% | 0.0362% | -3.742% | -0.01317%
2027 | 2025 Forecast | -0.002268% | -3.035% | 0% | -0.003155% | -3.042% | -0.654% | [5 empty] | 2025 Forecast | -1.451% | -8.914% | 0% | 0.3544% | -6.4% | -0.00175%
2028 | 2026 Forecast | -0.0001949% | -3.13% | 0% | -0.0003164% | -3.143% | -0.3829% | [5 empty] | 2026 Forecast | -1.472% | -9.786% | 0% | 0.1013% | -5.718% | 0.00087%
| Avg. Annual Growth | -0.1447% | -2.164% | 0% | -0.7898% | -2.967% | -0.5898% | [5 empty] | Avg. Annual Growth | -0.4931% | -10.34% | 0% | 0.5001% | -4.287% | -0.211%
| Washington Customers | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064
Residential
Commercial
General Service | Schedule 11 + Schedule 13 | 23048.75 | 23424.2976 | 23770.0833 | 24062.5417 | 24302.5701 | 24547.7146 | 24761.0741 | 24975.2387 | 25204.4889 | 25435.8434 | 25669.3215 | 25904.9427 | 26142.7267 | 26382.6933 | 26624.8627 | 26869.2549 | 27115.8904 | 27364.7898 | 27615.9739 | 27869.4637 | 28125.2802 | 28383.4449 | 28643.9793 | 28906.9052 | 29172.2445 | 29440.0194 | 29710.2523 | 29982.9656 | 30258.1821 | 30535.925 | 30816.2172 | 31099.0823 | 31384.5438 | 31672.6256 | 31963.3518 | 32256.7465 | 32552.8343 | 32851.64 | 33153.1884 | 33457.5048 | 33764.6145 | 34074.5432 | 34387.3168 | 34702.9613 | 35021.5032
Large General Service | Schedule 21 + Schedule 23 | 1751.4167 | 1676.2917 | 1593.2917 | 1575.125 | 1562.414 | 1549.9779 | 1537.977 | 1525.9773 | 1513.9773 | 1502.0716 | 1490.2596 | 1478.5404 | 1466.9135 | 1455.3779 | 1443.9331 | 1432.5782 | 1421.3127 | 1410.1357 | 1399.0467 | 1388.0448 | 1377.1294 | 1366.2999 | 1355.5556 | 1344.8957 | 1334.3197 | 1323.8269 | 1313.4165 | 1303.088 | 1292.8408 | 1282.6741 | 1272.5874 | 1262.58 | 1252.6512 | 1242.8006 | 1233.0274 | 1223.3311 | 1213.7111 | 1204.1666 | 1194.6973 | 1185.3024 | 1175.9814 | 1166.7337 | 1157.5587 | 1148.4558 | 1139.4246
Extra Large General Service | Schedule 25 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
Industrial
| Schedule 11 | 118.3333 | 118.3333 | 96.5 | 97.9167 | 98.4167 | 97.0268 | 97.0819 | 97.0729 | 97.0707 | 97.0685 | 97.0663 | 97.0641 | 97.0619 | 97.0597 | 97.0575 | 97.0553 | 97.0531 | 97.0509 | 97.0487 | 97.0465 | 97.0443 | 97.0421 | 97.0399 | 97.0377 | 97.0355 | 97.0333 | 97.0311 | 97.0289 | 97.0267 | 97.0245 | 97.0223 | 97.0201 | 97.0179 | 97.0157 | 97.0135 | 97.0113 | 97.0091 | 97.0069 | 97.0046 | 97.0024 | 97.0002 | 96.998 | 96.9958 | 96.9936 | 96.9914
| Schedule 21 | 71.3333 | 71.3333 | 70.4167 | 67.6667 | 68.5 | 66.9556 | 65.1867 | 63.2667 | 61.3467 | 59.4849 | 57.6797 | 55.9293 | 54.2319 | 52.5861 | 50.9902 | 49.4428 | 47.9423 | 46.4874 | 45.0766 | 43.7086 | 42.3822 | 41.096 | 39.8488 | 38.6395 | 37.4669 | 36.3298 | 35.2273 | 34.1582 | 33.1216 | 32.1164 | 31.1418 | 30.1967 | 29.2803 | 28.3917 | 27.5301 | 26.6946 | 25.8845 | 25.0989 | 24.3372 | 23.5987 | 22.8825 | 22.1881 | 21.5147 | 20.8618 | 20.2287
| Schedule 25 | 12 | 12 | 11.4167 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
Total
General Service | Schedule 11 + Schedule 13 | 23167.0833 | 23542.631 | 23866.5833 | 24160.4583 | 24400.9868 | 24644.7414 | 24858.156 | 25072.3116 | 25301.5596 | 25532.9119 | 25766.3878 | 26002.0068 | 26239.7886 | 26479.753 | 26721.9202 | 26966.3102 | 27212.9435 | 27461.8407 | 27713.0226 | 27966.5101 | 28222.3245 | 28480.487 | 28741.0192 | 29003.9429 | 29269.28 | 29537.0527 | 29807.2833 | 30079.9944 | 30355.2088 | 30632.9494 | 30913.2395 | 31196.1023 | 31481.5617 | 31769.6413 | 32060.3652 | 32353.7577 | 32649.8434 | 32948.6468 | 33250.1931 | 33554.5072 | 33861.6147 | 34171.5412 | 34484.3126 | 34799.955 | 35118.4947
Large General Service | Schedule 21 + Schedule 23 | 1822.75 | 1747.625 | 1663.7083 | 1642.7917 | 1630.914 | 1616.9335 | 1603.1637 | 1589.244 | 1575.3239 | 1561.5566 | 1547.9393 | 1534.4697 | 1521.1454 | 1507.964 | 1494.9233 | 1482.021 | 1469.255 | 1456.6231 | 1444.1233 | 1431.7534 | 1419.5116 | 1407.3959 | 1395.4044 | 1383.5352 | 1371.7866 | 1360.1567 | 1348.6438 | 1337.2462 | 1325.9624 | 1314.7905 | 1303.7291 | 1292.7766 | 1281.9315 | 1271.1923 | 1260.5575 | 1250.0257 | 1239.5955 | 1229.2656 | 1219.0345 | 1208.9011 | 1198.8639 | 1188.9217 | 1179.0734 | 1169.3176 | 1159.6533
Extra Large General Service | Schedule 25 | 22 | 22 | 21.4167 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
|  | 25011.8333 | 25312.256 | 25551.7083 | 25824.25 | 26052.9008 | 26282.6748 | 26482.3197 | 26682.5556 | 26897.8835 | 27115.4684 | 27335.327 | 27557.4765 | 27781.934 | 28008.717 | 28237.8435 | 28469.3312 | 28703.1985 | 28939.4638 | 29178.1459 | 29419.2635 | 29662.8361 | 29908.8829 | 30157.4236 | 30408.4781 | 30662.0666 | 30918.2094 | 31176.9271 | 31438.2407 | 31702.1712 | 31968.7399 | 32237.9686 | 32509.879 | 32784.4932 | 33061.8336 | 33341.9227 | 33624.7835 | 33910.4389 | 34198.9124 | 34490.2276 | 34784.4083 | 35081.4786 | 35381.463 | 35684.386 | 35990.2726 | 36299.1479
| Idaho Customers | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064
Commercial
| Schedule 11 | 16524.1667 | 16848.4167 | 17165.3333 | 17598.4167 | 17867 | 18134.5 | 18401.9167 | 18671.5833 | 18941.4167 | 19215.1495 | 19492.8382 | 19774.54 | 20060.3127 | 20350.2154 | 20644.3075 | 20942.6498 | 21245.3035 | 21552.3311 | 21863.7957 | 22179.7615 | 22500.2934 | 22825.4576 | 23155.3208 | 23489.9511 | 23829.4173 | 24173.7894 | 24523.1381 | 24877.5355 | 25237.0544 | 25601.769 | 25971.7543 | 26347.0864 | 26727.8427 | 27114.1014 | 27505.9422 | 27903.4458 | 28306.6938 | 28715.7694 | 29130.7568 | 29551.7415 | 29978.8099 | 30412.0502 | 30851.5515 | 31297.4043 | 31749.7003
| Schedule 21 | 878.5 | 790.9167 | 710.6667 | 631.8056 | 608.9167 | 584.9167 | 560.9167 | 536.9167 | 512.9167 | 489.9895 | 468.0871 | 447.1637 | 427.1757 | 408.0811 | 389.84 | 372.4143 | 355.7675 | 339.8648 | 324.6729 | 310.1601 | 296.2961 | 283.0518 | 270.3994 | 258.3127 | 246.7662 | 235.7358 | 225.1985 | 215.1322 | 205.5159 | 196.3294 | 187.5535 | 179.1699 | 171.1611 | 163.5102 | 156.2014 | 149.2192 | 142.5492 | 136.1773 | 130.0902 | 124.2752 | 118.7202 | 113.4134 | 108.3439 | 103.5009 | 98.8745
| Schedule 25 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Industrial
| Schedule 11 | 119.5417 | 119.5417 | 114.5 | 115.8333 | 116.75 | 119.6139 | 117.4967 | 115.8167 | 114.1367 | 112.481 | 110.8494 | 109.2415 | 107.6569 | 106.0952 | 104.5562 | 103.0396 | 101.5449 | 100.0719 | 98.6203 | 97.1898 | 95.78 | 94.3906 | 93.0214 | 91.6721 | 90.3423 | 89.0318 | 87.7404 | 86.4676 | 85.2134 | 83.9773 | 82.7591 | 81.5587 | 80.3756 | 79.2097 | 78.0607 | 76.9284 | 75.8125 | 74.7128 | 73.629 | 72.561 | 71.5084 | 70.4711 | 69.4489 | 68.4415 | 67.4487
| Schedule 21 | 54.4167 | 54.4167 | 46.5833 | 45.25 | 41.5833 | 34.2306 | 32.2567 | 29.6167 | 26.9767 | 24.572 | 22.3817 | 20.3866 | 18.5694 | 16.9141 | 15.4064 | 14.0331 | 12.7822 | 11.6428 | 10.605 | 9.6597 | 8.7986 | 8.0143 | 7.2999 | 6.6492 | 6.0565 | 5.5166 | 5.0249 | 4.577 | 4.169 | 3.7974 | 3.4589 | 3.1506 | 2.8697 | 2.6139 | 2.3809 | 2.1687 | 1.9754 | 1.7993 | 1.6389 | 1.4928 | 1.3597 | 1.2385 | 1.1281 | 1.0276 | 0.93597
| Schedule 25 | 8.0833 | 8.0833 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
Total
General Service | Schedule 11 | 16643.7083 | 16967.9583 | 17279.8333 | 17714.25 | 17983.75 | 18254.1139 | 18519.4133 | 18787.4 | 19055.5533 | 19327.6305 | 19603.6876 | 19883.7814 | 20167.9696 | 20456.3106 | 20748.8638 | 21045.6894 | 21346.8485 | 21652.4031 | 21962.4161 | 22276.9513 | 22596.0734 | 22919.8482 | 23248.3422 | 23581.6232 | 23919.7596 | 24262.8212 | 24610.8785 | 24964.0031 | 25322.2678 | 25685.7463 | 26054.5134 | 26428.6451 | 26808.2182 | 27193.3111 | 27584.0029 | 27980.3741 | 28382.5063 | 28790.4822 | 29204.3858 | 29624.3024 | 30050.3184 | 30482.5214 | 30921.0004 | 31365.8458 | 31817.149
Large General Service | Schedule 21 | 932.9167 | 845.3333 | 757.25 | 677.0556 | 650.5 | 619.1472 | 593.1733 | 566.5333 | 539.8933 | 514.5615 | 490.4688 | 467.5503 | 445.745 | 424.9952 | 405.2464 | 386.4473 | 368.5496 | 351.5076 | 335.2779 | 319.8198 | 305.0947 | 291.0661 | 277.6993 | 264.9619 | 252.8227 | 241.2524 | 230.2234 | 219.7092 | 209.6848 | 200.1267 | 191.0124 | 182.3205 | 174.0308 | 166.1242 | 158.5823 | 151.3879 | 144.5245 | 137.9766 | 131.7291 | 125.768 | 120.0799 | 114.6519 | 109.472 | 104.5285 | 99.8104
Extra Large General Service | Schedule 25 | 11.0833 | 11.0833 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
|  | 17587.7083 | 17824.375 | 18048.0833 | 18402.3056 | 18645.25 | 18884.2611 | 19123.5867 | 19364.9333 | 19606.4467 | 19853.192 | 20105.1564 | 20362.3318 | 20624.7146 | 20892.3057 | 21165.1101 | 21443.1367 | 21726.3981 | 22014.9106 | 22308.6939 | 22607.7711 | 22912.1681 | 23221.9142 | 23537.0416 | 23857.5851 | 24183.5823 | 24515.0736 | 24852.1018 | 25194.7123 | 25542.9526 | 25896.873 | 26256.5258 | 26621.9655 | 26993.249 | 27370.4353 | 27753.5852 | 28142.762 | 28538.0308 | 28939.4588 | 29347.1149 | 29761.0704 | 30181.3983 | 30608.1733 | 31041.4724 | 31481.3743 | 31927.9595
| Washington Sales (MWh) | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064
Commercial
| Schedule 11 + Schedule 13 | 527691.9884 | 580954.9948 | 612657.9839 | 618353.7036 | 610527.5917 | 609127.1577 | 614390.5599 | 619675.1287 | 625371.5714 | 629145.8498 | 632942.9068 | 636762.88 | 640605.9078 | 644472.1293 | 648361.6843 | 652274.7139 | 656211.3596 | 660171.7639 | 664156.0704 | 668164.4231 | 672196.9672 | 676253.8489 | 680335.2148 | 684441.2128 | 688571.9916 | 692727.7007 | 696908.4906 | 701114.5126 | 705345.919 | 709602.8631 | 713885.4989 | 718193.9815 | 722528.4669 | 726889.1121 | 731276.0749 | 735689.5141 | 740129.5895 | 744596.462 | 749090.2932 | 753611.2458 | 758159.4835 | 762735.171 | 767338.474 | 771969.5591 | 776628.5939
| Schedule 21 + Schedule 23 | 1148654.6453 | 1190232.5918 | 1196881.8536 | 1176318.2176 | 1161909.9513 | 1147240.437 | 1130995.7066 | 1110531.7953 | 1087177.3342 | 1069263.6772 | 1051645.1875 | 1034317.0014 | 1017274.3356 | 1000512.4856 | 984026.8241 | 967812.8005 | 951865.9389 | 936181.8372 | 920756.1658 | 905584.6666 | 890663.1515 | 875987.5014 | 861553.6651 | 847357.6584 | 833395.5623 | 819663.5227 | 806157.7489 | 792874.5126 | 779810.1472 | 766961.0461 | 754323.6624 | 741894.5077 | 729670.1508 | 717647.2173 | 705822.3883 | 694192.3996 | 682754.0407 | 671504.1542 | 660439.6345 | 649557.4272 | 638854.5285 | 628327.9837 | 617974.8872 | 607792.3808 | 597777.6538
| Schedule 25 | 269999.573 | 279253.0918 | 285594.1585 | 283828.8352 | 284952.4405 | 286093.36 | 287014.03 | 287562.79 | 287967.9 | 288726.89 | 289487.8804 | 290250.8766 | 291015.8837 | 291782.9072 | 292551.9523 | 293323.0244 | 294096.1287 | 294871.2707 | 295648.4557 | 296427.6892 | 297208.9764 | 297992.3229 | 298777.734 | 299565.2152 | 300354.7719 | 301146.4096 | 301940.1339 | 302735.9502 | 303533.8639 | 304333.8807 | 305136.0061 | 305940.2457 | 306746.6049 | 307555.0895 | 308365.7049 | 309178.4569 | 309993.351 | 310810.393 | 311629.5883 | 312450.9428 | 313274.4622 | 314100.1521 | 314928.0182 | 315758.0663 | 316590.3021
% Change
| Schedule 11 | 2021: 10.09%; 2022: 5.457%; 2023: 0.9297%; 2024: -1.266%; 2025: -0.2294%; 2026: 0.8641%; 2027: 0.8601%; 2028: 0.9193%; 2029: 0.6035%
| Schedule 21 | 2021: 3.62%; 2022: 0.5587%; 2023: -1.718%; 2024: -1.225%; 2025: -1.263%; 2026: -1.416%; 2027: -1.809%; 2028: -2.103%; 2029: -1.648%
| Schedule 25 | 2021: 3.427%; 2022: 2.271%; 2023: -0.6181%; 2024: 0.3959%; 2025: 0.4004%; 2026: 0.3218%; 2027: 0.1912%; 2028: 0.1409%; 2029: 0.2636%
Industrial
| Schedule 11 | 5842.1184 | 5292.3865 | 5097.8251 | 5056.5861 | 5085.4258 | 4862.6511 | 4862.0419 | 4861.8886 | 4861.8732 | 4808.4333 | 4755.5808 | 4703.3093 | 4651.6123 | 4600.4835 | 4549.9168 | 4499.9058 | 4450.4445 | 4401.5269 | 4353.147 | 4305.2989 | 4257.9767 | 4211.1746 | 4164.887 | 4119.1081 | 4073.8324 | 4029.0544 | 3984.7685 | 3940.9695 | 3897.6518 | 3854.8103 | 3812.4397 | 3770.5348 | 3729.0905 | 3688.1018 | 3647.5636 | 3607.4709 | 3567.819 | 3528.6028 | 3489.8178 | 3451.459 | 3413.5219 | 3376.0017 | 3338.894 | 3302.1942 | 3265.8977
| Schedule 21 | 85559.8213 | 91492.006 | 94578.5639 | 89533.2106 | 89323.8704 | 86858.9272 | 84289.4053 | 81724.9209 | 79156.0904 | 76800.4908 | 74514.9912 | 72297.5057 | 70146.0101 | 68058.5407 | 66033.1921 | 64068.1158 | 62161.5179 | 60311.6584 | 58516.8486 | 56775.4505 | 55085.8745 | 53446.5785 | 51856.0661 | 50312.8856 | 48815.6286 | 47362.9283 | 45953.4587 | 44585.9335 | 43259.1043 | 41971.7602 | 40722.726 | 39510.8617 | 38335.0612 | 37194.2512 | 36087.3905 | 35013.4688 | 33971.5059 | 32960.5506 | 31979.6802 | 31027.9995 | 30104.6398 | 29208.7583 | 28339.5372 | 27496.1833 | 26677.9266
| Schedule 25 | 293266.573 | 303454.2909 | 337897.3954 | 342893.2432 | 339923.2227 | 333173.665 | 329558.911 | 327403.571 | 326149.846 | 322800.6986 | 319485.9426 | 316205.2251 | 312958.1963 | 309744.5105 | 306563.8252 | 303415.8014 | 300300.104 | 297216.4008 | 294164.3633 | 291143.6664 | 288153.9883 | 285195.0104 | 282266.4174 | 279367.8974 | 276499.1416 | 273659.8442 | 270849.7029 | 268068.4181 | 265315.6937 | 262591.2362 | 259894.7555 | 257225.9643 | 254584.5781 | 251970.3157 | 249382.8985 | 246822.0507 | 244287.4997 | 241778.9752 | 239296.2102 | 236838.94 | 234406.9029 | 231999.8397 | 229617.4941 | 227259.6121 | 224925.9426
% Change
| Schedule 11 | 2021: -9.41%; 2022: -3.676%; 2023: -0.809%; 2024: 0.5703%; 2025: -4.381%; 2026: -0.01253%; 2027: -0.003155%; 2028: -0.0003164%; 2029: -1.099%
| Schedule 21 | 2021: 6.933%; 2022: 3.374%; 2023: -5.335%; 2024: -0.2338%; 2025: -2.76%; 2026: -2.958%; 2027: -3.042%; 2028: -3.143%; 2029: -2.976%
| Schedule 25 | 2021: 3.474%; 2022: 11.35%; 2023: 1.479%; 2024: -0.8662%; 2025: -1.986%; 2026: -1.085%; 2027: -0.654%; 2028: -0.3829%; 2029: -1.027%
Total
| Schedule 11 + Schedule 13 | 533534.1068 | 586247.3812 | 617755.809 | 623410.2897 | 615613.0175 | 613989.8088 | 619252.6018 | 624537.0173 | 630233.4446 | 633954.2831 | 637698.4876 | 641466.1893 | 645257.5201 | 649072.6128 | 652911.6011 | 656774.6197 | 660661.8041 | 664573.2909 | 668509.2174 | 672469.722 | 676454.9439 | 680465.0234 | 684500.1017 | 688560.3209 | 692645.824 | 696756.7551 | 700893.2591 | 705055.4821 | 709243.5708 | 713457.6734 | 717697.9386 | 721964.5163 | 726257.5574 | 730577.2139 | 734923.6384 | 739296.985 | 743697.4085 | 748125.0648 | 752580.111 | 757062.7048 | 761573.0054 | 766111.1728 | 770677.368 | 775271.7532 | 779894.4916
| Schedule 21 + Schedule 23 | 1234214.4666 | 1281724.5978 | 1291460.4175 | 1265851.4282 | 1251233.8217 | 1234099.3643 | 1215285.1118 | 1192256.7162 | 1166333.4246 | 1146064.168 | 1126160.1787 | 1106614.5071 | 1087420.3458 | 1068571.0263 | 1050060.0163 | 1031880.9163 | 1014027.4568 | 996493.4956 | 979273.0145 | 962360.1171 | 945749.026 | 929434.0798 | 913409.7312 | 897670.544 | 882211.1908 | 867026.4509 | 852111.2076 | 837460.4461 | 823069.2515 | 808932.8063 | 795046.3884 | 781405.3694 | 768005.212 | 754841.4686 | 741909.7789 | 729205.8684 | 716725.5466 | 704464.7048 | 692419.3147 | 680585.4268 | 668959.1683 | 657536.7421 | 646314.4244 | 635288.564 | 624455.5804
| Schedule 25 | 563266.1459 | 582707.3827 | 623491.554 | 626722.0783 | 624875.6632 | 619267.025 | 616572.941 | 614966.361 | 614117.746 | 611527.5885 | 608973.823 | 606456.1016 | 603974.0801 | 601527.4177 | 599115.7775 | 596738.8258 | 594396.2327 | 592087.6715 | 589812.819 | 587571.3556 | 585362.9647 | 583187.3332 | 581044.1514 | 578933.1126 | 576853.9135 | 574806.2539 | 572789.8368 | 570804.3683 | 568849.5576 | 566925.117 | 565030.7617 | 563166.2099 | 561331.1831 | 559525.4052 | 557748.6034 | 556000.5076 | 554280.8507 | 552589.3682 | 550925.7985 | 549289.8829 | 547681.3651 | 546099.9918 | 544545.5123 | 543017.6784 | 541516.2447
|  | 2331014.7194 | 2450679.3617 | 2532707.7804 | 2515983.7963 | 2491722.5025 | 2467356.1981 | 2451110.6547 | 2431760.0945 | 2410684.6152 | 2391546.0396 | 2372832.4894 | 2354536.7981 | 2336651.946 | 2319171.0568 | 2302087.3949 | 2285394.3618 | 2269085.4936 | 2253154.4579 | 2237595.0509 | 2222401.1946 | 2207566.9345 | 2193086.4365 | 2178953.9843 | 2165163.9775 | 2151710.9283 | 2138589.4599 | 2125794.3035 | 2113320.2965 | 2101162.3799 | 2089315.5966 | 2077775.0886 | 2066536.0956 | 2055593.9525 | 2044944.0876 | 2034582.0207 | 2024503.3611 | 2014703.8058 | 2005179.1378 | 1995925.2242 | 1986938.0145 | 1978213.5388 | 1969747.9066 | 1961537.3047 | 1953577.9957 | 1945866.3167
| Idaho Sales (MWh) | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064
Commercial
| Schedule 11 | 363872.1507 | 399763.9599 | 429904.05 | 457007.8954 | 452091.539 | 459010.708 | 464497.593 | 471064.584 | 477514.084 | 484090.3698 | 490757.2237 | 497515.893 | 504367.6421 | 511313.753 | 518355.5252 | 525494.2761 | 532731.3413 | 540068.0747 | 547505.8491 | 555046.0559 | 562690.1059 | 570439.4291 | 578295.4753 | 586259.7144 | 594333.6364 | 602518.7517 | 610816.5918 | 619228.7091 | 627756.6775 | 636402.0923 | 645166.5711 | 654051.7535 | 663059.302 | 672190.9018 | 681448.2612 | 690833.1122 | 700347.2106 | 709992.3365 | 719770.2942 | 729682.9132 | 739732.048 | 749919.5787 | 760247.4112 | 770717.4778 | 781331.7374
| Schedule 21 | 511154.28 | 511727.6649 | 504797.0852 | 494888.6053 | 489440.7564 | 483085.698 | 475916.8838 | 467722.0251 | 458446.1452 | 451010.7114 | 443695.8713 | 436499.6688 | 429420.1799 | 422455.5116 | 415603.8017 | 408863.2182 | 402231.9586 | 395708.2499 | 389290.3478 | 382976.5361 | 376765.1267 | 370654.4588 | 364642.8984 | 358728.8381 | 352910.6967 | 347186.9183 | 341555.9726 | 336016.354 | 330566.5811 | 325205.1969 | 319930.7677 | 314741.8833 | 309637.1563 | 304615.2216 | 299674.7366 | 294814.3802 | 290032.8528 | 285328.8759 | 280701.1917 | 276148.5629 | 271669.7722 | 267263.6219 | 262928.934 | 258664.5494 | 254469.3278
| Schedule 25 | 60263.9681 | 63232.1426 | 61039.6729 | 55616.767 | 60013.017 | 60169.344 | 60602.688 | 60877.626 | 61153.89 | 61442.5625 | 61732.5976 | 62024.0019 | 62316.7817 | 62610.9435 | 62906.4939 | 63203.4394 | 63501.7867 | 63801.5422 | 64102.7128 | 64405.305 | 64709.3255 | 65014.7812 | 65321.6787 | 65630.025 | 65939.8267 | 66251.0909 | 66563.8244 | 66878.034 | 67193.7269 | 67510.91 | 67829.5904 | 68149.775 | 68471.4711 | 68794.6857 | 69119.426 | 69445.6992 | 69773.5126 | 70102.8734 | 70433.7889 | 70766.2665 | 71100.3135 | 71435.9374 | 71773.1455 | 72111.9454 | 72452.3446
% Change
| Schedule 11 | 2021: 9.864%; 2022: 7.539%; 2023: 6.305%; 2024: -1.076%; 2025: 1.53%; 2026: 1.195%; 2027: 1.414%; 2028: 1.369%; 2029: 1.377%
| Schedule 21 | 2021: 0.1122%; 2022: -1.354%; 2023: -1.963%; 2024: -1.101%; 2025: -1.298%; 2026: -1.484%; 2027: -1.722%; 2028: -1.983%; 2029: -1.622%
| Schedule 25 | 2021: 4.925%; 2022: -3.467%; 2023: -8.884%; 2024: 7.905%; 2025: 0.2605%; 2026: 0.7202%; 2027: 0.4537%; 2028: 0.4538%; 2029: 0.472%
Industrial
| Schedule 11 | 5057.5732 | 5478.4161 | 5889.2016 | 6178.5296 | 5999.3659 | 6038.8728 | 6041.0588 | 6062.466 | 6068.6068 | 6086.0597 | 6103.5628 | 6121.1162 | 6138.7201 | 6156.3746 | 6174.0799 | 6191.8361 | 6209.6434 | 6227.5019 | 6245.4117 | 6263.3731 | 6281.3861 | 6299.4509 | 6317.5677 | 6335.7366 | 6353.9577 | 6372.2312 | 6390.5573 | 6408.9361 | 6427.3677 | 6445.8524 | 6464.3902 | 6482.9813 | 6501.6259 | 6520.3241 | 6539.0761 | 6557.882 | 6576.742 | 6595.6563 | 6614.6249 | 6633.6481 | 6652.726 | 6671.8587 | 6691.0465 | 6710.2895 | 6729.5878
| Schedule 21 | 60018.7396 | 59284.9371 | 57616.5692 | 60860.3356 | 55147.09 | 52442.7488 | 50480.5534 | 47249.9276 | 44548.0825 | 42235.6576 | 40043.2672 | 37964.6805 | 35993.9902 | 34125.5956 | 32354.1865 | 30674.7286 | 29082.4489 | 27572.8221 | 26141.5577 | 24784.5882 | 23498.057 | 22278.3077 | 21121.8737 | 20025.4686 | 18985.9762 | 18000.4423 | 17066.066 | 16180.1918 | 15340.302 | 14544.0097 | 13789.0517 | 13073.2825 | 12394.6678 | 11751.2789 | 11141.2874 | 10562.9597 | 10014.6521 | 9494.8064 | 9001.9451 | 8534.6674 | 8091.6455 | 7671.6202 | 7273.3977 | 6895.8464 | 6537.8933
| Schedule 25 | 270693.1646 | 281585.3933 | 290907.2059 | 283599.2579 | 287343.343 | 287287.315 | 287249.487 | 287244.461 | 287246.96 | 287222.8703 | 287198.7826 | 287174.6969 | 287150.6133 | 287126.5317 | 287102.4521 | 287078.3745 | 287054.2989 | 287030.2254 | 287006.1538 | 286982.0843 | 286958.0168 | 286933.9513 | 286909.8879 | 286885.8264 | 286861.767 | 286837.7096 | 286813.6542 | 286789.6009 | 286765.5495 | 286741.5002 | 286717.4529 | 286693.4076 | 286669.3643 | 286645.323 | 286621.2838 | 286597.2465 | 286573.2113 | 286549.1781 | 286525.1469 | 286501.1178 | 286477.0906 | 286453.0655 | 286429.0423 | 286405.0212 | 286381.0021
% Change
| Schedule 11 | 2021: 8.321%; 2022: 7.498%; 2023: 4.913%; 2024: -2.9%; 2025: 0.6585%; 2026: 0.0362%; 2027: 0.3544%; 2028: 0.1013%; 2029: 0.2876%
| Schedule 21 | 2021: -1.223%; 2022: -2.814%; 2023: 5.63%; 2024: -9.387%; 2025: -4.904%; 2026: -3.742%; 2027: -6.4%; 2028: -5.718%; 2029: -5.191%
| Schedule 25 | 2021: 4.024%; 2022: 3.31%; 2023: -2.512%; 2024: 1.32%; 2025: -0.0195%; 2026: -0.01317%; 2027: -0.00175%; 2028: 0.00087%; 2029: -0.008386%
Total
| Schedule 11 | 368929.724 | 405242.376 | 435793.2516 | 463186.425 | 458090.9049 | 465049.5808 | 470538.6518 | 477127.05 | 483582.6908 | 490176.4295 | 496860.7865 | 503637.0092 | 510506.3622 | 517470.1276 | 524529.6051 | 531686.1122 | 538940.9846 | 546295.5766 | 553751.2608 | 561309.429 | 568971.492 | 576738.88 | 584613.043 | 592595.451 | 600687.594 | 608890.9829 | 617207.1491 | 625637.6452 | 634184.0452 | 642847.9447 | 651630.9612 | 660534.7348 | 669560.9279 | 678711.2259 | 687987.3373 | 697390.9942 | 706923.9526 | 716587.9927 | 726384.9191 | 736316.5613 | 746384.774 | 756591.4374 | 766938.4577 | 777427.7673 | 788061.3252
| Schedule 21 | 571173.0196 | 571012.6021 | 562413.6545 | 555748.9409 | 544587.8464 | 535528.4468 | 526397.4372 | 514971.9527 | 502994.2278 | 493246.369 | 483739.1384 | 474464.3493 | 465414.1701 | 456581.1072 | 447957.9882 | 439537.9468 | 431314.4075 | 423281.072 | 415431.9055 | 407761.1243 | 400263.1837 | 392932.7665 | 385764.7721 | 378754.3067 | 371896.6729 | 365187.3606 | 358622.0386 | 352196.5458 | 345906.8831 | 339749.2066 | 333719.8194 | 327815.1658 | 322031.824 | 316366.5006 | 310816.0241 | 305377.3399 | 300047.5049 | 294823.6823 | 289703.1368 | 284683.2304 | 279761.4177 | 274935.2421 | 270202.3317 | 265560.3958 | 261007.2211
| Schedule 25 | 330957.1327 | 344817.5359 | 351946.8788 | 339216.0249 | 347356.36 | 347456.659 | 347852.175 | 348122.087 | 348400.85 | 348665.4328 | 348931.3802 | 349198.6988 | 349467.395 | 349737.4752 | 350008.946 | 350281.8139 | 350556.0856 | 350831.7676 | 351108.8666 | 351387.3893 | 351667.3424 | 351948.7325 | 352231.5666 | 352515.8514 | 352801.5938 | 353088.8005 | 353377.4786 | 353667.6349 | 353959.2765 | 354252.4102 | 354547.0433 | 354843.1826 | 355140.8354 | 355440.0087 | 355740.7098 | 356042.9458 | 356346.7239 | 356652.0515 | 356958.9358 | 357267.3842 | 357577.4041 | 357889.0028 | 358202.1878 | 358516.9666 | 358833.3467
|  | 1271059.8763 | 1321072.514 | 1350153.7848 | 1358151.3908 | 1350035.1113 | 1348034.6866 | 1344788.2641 | 1340221.0897 | 1334977.7686 | 1332088.2313 | 1329531.3052 | 1327300.0573 | 1325387.9273 | 1323788.71 | 1322496.5392 | 1321505.8728 | 1320811.4777 | 1320408.4162 | 1320292.0329 | 1320457.9426 | 1320902.0181 | 1321620.379 | 1322609.3818 | 1323865.6091 | 1325385.8607 | 1327167.1441 | 1329206.6664 | 1331501.8259 | 1334050.2048 | 1336849.5615 | 1339897.8239 | 1343193.0833 | 1346733.5874 | 1350517.7352 | 1354544.0711 | 1358811.2799 | 1363318.1815 | 1368063.7265 | 1373046.9917 | 1378267.1759 | 1383723.5957 | 1389415.6823 | 1395342.9773 | 1401505.1297 | 1407901.893
*Next year use the growth rate from average of previous 4 years, and apply through the end of the forecast
Winter Load Factors | bar: 2020
| Washington | 2022: Sector; 2023: Summer % of Winter Demand
General Service | Schedule 11 | 2020: 0.5839; 2022: Residential; 2023: 107.7%
Large General Service | Schedule 21 | 2020: 0.66176; 2022: Commercial; 2023: 100.5%
Extra Large General Service | Schedule 25 | 2020: 0.82; 2022: Industrial; 2023: 89.39%
| Idaho | 2022: Sector; 2023: Summer % of Winter Demand
General Service | Schedule 11 | 2020: 0.63256; 2022: Residential; 2023: 104.8%
Large General Service | Schedule 21 | 2020: 0.64229; 2022: Commercial; 2023: 98.94%
Extra Large General Service | Schedule 25 | 2020: 0.77; 2022: Industrial; 2023: 96.74%
| Source: EE peak control totals. \\EgnyteDrive\Ameresco Files\AEG\Clients\Avista Energy\1341 Avista CPA\X_2010 CPA\Utility provided data and Background documents\Load Research Report 2009 KEMA\2009 COS Report V01_3-15-10 KEMA jb annotations.doc | 2020: 2010 KEMA Study
[7 empty] | Start Year | [22 empty] | End Year
Washington Winter Peak (MW) | Segment | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064
Schedule 11 + Schedule 13 | General Service | 104.3079 | 114.6135 | 120.7735 | 121.879 | 120.3546 | 120.0373 | 121.0661 | 122.0993 | 123.2129 | 123.9404 | 124.6724 | 125.409 | 126.1502 | 126.8961 | 127.6466 | 128.4018 | 129.1618 | 129.9265 | 130.696 | 131.4703 | 132.2494 | 133.0334 | 133.8223 | 134.6161 | 135.4148 | 136.2185 | 137.0272 | 137.8409 | 138.6597 | 139.4836 | 140.3126 | 141.1467 | 141.986 | 142.8305 | 143.6803 | 144.5353 | 145.3956 | 146.2612 | 147.1322 | 148.0085 | 148.8903 | 149.7775 | 150.6702 | 151.5685 | 152.4722
Schedule 21 + Schedule 23 | Large General Service | 212.906 | 221.1016 | 222.7811 | 218.3635 | 215.8419 | 212.8861 | 209.6406 | 205.6681 | 201.1963 | 197.6998 | 194.2663 | 190.8946 | 187.5835 | 184.332 | 181.1387 | 178.0028 | 174.923 | 171.8983 | 168.9278 | 166.0102 | 163.1448 | 160.3304 | 157.5661 | 154.8511 | 152.1843 | 149.5649 | 146.9919 | 144.4646 | 141.9821 | 139.5435 | 137.1481 | 134.7949 | 132.4834 | 130.2126 | 127.9818 | 125.7904 | 123.6375 | 121.5224 | 119.4446 | 117.4032 | 115.3976 | 113.4272 | 111.4913 | 109.5893 | 107.7206
Schedule 25 | Extra Large General Service | 78.4144 | 81.1209 | 86.7986 | 87.2483 | 86.9913 | 86.2105 | 85.8354 | 85.6118 | 85.4936 | 85.133 | 84.7775 | 84.427 | 84.0815 | 83.7409 | 83.4051 | 83.0742 | 82.7481 | 82.4267 | 82.11 | 81.798 | 81.4906 | 81.1877 | 80.8893 | 80.5954 | 80.306 | 80.0209 | 79.7402 | 79.4638 | 79.1917 | 78.9238 | 78.66 | 78.4005 | 78.145 | 77.8936 | 77.6463 | 77.4029 | 77.1635 | 76.928 | 76.6964 | 76.4687 | 76.2448 | 76.0246 | 75.8082 | 75.5955 | 75.3865
| C&I Total | 395.6282 | 416.836 | 430.3532 | 427.4908 | 423.1877 | 419.1338 | 416.5422 | 413.3792 | 409.9028 | 406.7732 | 403.7162 | 400.7306 | 397.8152 | 394.9689 | 392.1905 | 389.4789 | 386.8329 | 384.2516 | 381.7338 | 379.2785 | 376.8847 | 374.5515 | 372.2777 | 370.0626 | 367.9051 | 365.8043 | 363.7593 | 361.7694 | 359.8335 | 357.9509 | 356.1207 | 354.3421 | 352.6144 | 350.9367 | 349.3083 | 347.7285 | 346.1965 | 344.7116 | 343.2732 | 341.8804 | 340.5327 | 339.2294 | 337.9698 | 336.7533 | 335.5793
| Residential Total | 463.5726 | 486.7262 | 505.9826 | 502.0448 | 502.4712 | 512.3676 | 520.584 | 529.8971 | 539.1528 | 546.9099 | 554.7786 | 562.7605 | 570.8572 | 579.0704 | 587.4018 | 595.8531 | 604.4259 | 613.1221 | 621.9435 | 630.8917 | 639.9687 | 649.1762 | 658.5163 | 667.9907 | 677.6014 | 687.3504 | 697.2397 | 707.2713 | 717.4472 | 727.7695 | 738.2403 | 748.8617 | 759.636 | 770.5653 | 781.6518 | 792.8979 | 804.3057 | 815.8777 | 827.6161 | 839.5235 | 851.6022 | 863.8546 | 876.2834 | 888.8909 | 901.6799
| Total Res and C&I (Winter) |  |  | 936.3358 | 929.5356 | 925.659 | 931.5014 | 937.1262 | 943.2762 | 949.0557 | 953.6831 | 958.4947 | 963.491 | 968.6724 | 974.0393 | 979.5923 | 985.332 | 991.2589 | 997.3737 | 1003.6772 | 1010.1702 | 1016.8534 | 1023.7277 | 1030.794 | 1038.0533 | 1045.5065 | 1053.1547 | 1060.9991 | 1069.0406 | 1077.2807 | 1085.7203 | 1094.3609 | 1103.2038 | 1112.2504 | 1121.502 | 1130.9602 | 1140.6264 | 1150.5022 | 1160.5893 | 1170.8893 | 1181.4039 | 1192.1349 | 1203.084 | 1214.2531 | 1225.6442 | 1237.2592
Idaho Winter Peak (MW) | Segment | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064
Schedule 11 | General Service | 66.5789 | 73.132 | 78.6454 | 83.5889 | 82.6693 | 83.9251 | 84.9157 | 86.1047 | 87.2697 | 88.4596 | 89.6659 | 90.8888 | 92.1285 | 93.3852 | 94.6592 | 95.9507 | 97.2599 | 98.5872 | 99.9327 | 101.2967 | 102.6794 | 104.0811 | 105.5021 | 106.9427 | 108.403 | 109.8835 | 111.3842 | 112.9056 | 114.448 | 116.0115 | 117.5965 | 119.2033 | 120.8323 | 122.4836 | 124.1576 | 125.8546 | 127.575 | 129.319 | 131.087 | 132.8793 | 134.6963 | 136.5382 | 138.4055 | 140.2984 | 142.2174
Schedule 21 | Large General Service | 101.5149 | 101.4864 | 99.9581 | 98.7736 | 96.7899 | 95.1798 | 93.5569 | 91.5263 | 89.3975 | 87.665 | 85.9752 | 84.3268 | 82.7183 | 81.1484 | 79.6158 | 78.1193 | 76.6578 | 75.23 | 73.835 | 72.4716 | 71.139 | 69.8362 | 68.5622 | 67.3162 | 66.0974 | 64.905 | 63.7381 | 62.5961 | 61.4782 | 60.3838 | 59.3122 | 58.2628 | 57.2349 | 56.228 | 55.2415 | 54.2749 | 53.3276 | 52.3992 | 51.4891 | 50.5969 | 49.7222 | 48.8644 | 48.0232 | 47.1982 | 46.389
Schedule 25 | Extra Large General Service | 49.0656 | 51.1204 | 52.1774 | 50.29 | 51.4968 | 51.5117 | 51.5703 | 51.6103 | 51.6517 | 51.6909 | 51.7303 | 51.77 | 51.8098 | 51.8498 | 51.8901 | 51.9305 | 51.9712 | 52.0121 | 52.0531 | 52.0944 | 52.1359 | 52.1777 | 52.2196 | 52.2617 | 52.3041 | 52.3467 | 52.3895 | 52.4325 | 52.4757 | 52.5192 | 52.5629 | 52.6068 | 52.6509 | 52.6953 | 52.7398 | 52.7846 | 52.8297 | 52.8749 | 52.9204 | 52.9662 | 53.0121 | 53.0583 | 53.1048 | 53.1514 | 53.1983
| C&I Total | 217.1594 | 225.7389 | 230.7809 | 232.6525 | 230.9561 | 230.6166 | 230.043 | 229.2413 | 228.3188 | 227.8155 | 227.3715 | 226.9856 | 226.6566 | 226.3835 | 226.1651 | 226.0006 | 225.8889 | 225.8292 | 225.8208 | 225.8627 | 225.9543 | 226.095 | 226.2839 | 226.5207 | 226.8046 | 227.1351 | 227.5118 | 227.9342 | 228.4019 | 228.9145 | 229.4716 | 230.0729 | 230.7181 | 231.4068 | 232.1389 | 232.9141 | 233.7323 | 234.5931 | 235.4965 | 236.4424 | 237.4306 | 238.4609 | 239.5335 | 240.6481 | 241.8047
| Residential Total | 214.2386 | 225.1906 | 238.2555 | 239.1271 | 241.9787 | 244.812 | 246.9435 | 249.6378 | 252.7334 | 255.5464 | 258.3907 | 261.2667 | 264.1747 | 267.115 | 270.0881 | 273.0943 | 276.1339 | 279.2073 | 282.315 | 285.4572 | 288.6345 | 291.8471 | 295.0954 | 298.3799 | 301.701 | 305.059 | 308.4544 | 311.8876 | 315.359 | 318.869 | 322.4181 | 326.0067 | 329.6353 | 333.3042 | 337.014 | 340.7651 | 344.5579 | 348.3929 | 352.2706 | 356.1915 | 360.156 | 364.1647 | 368.218 | 372.3163 | 376.4603
| Total Res and C&I (Winter) |  |  | 469.0364 | 471.7796 | 472.9348 | 475.4286 | 476.9864 | 478.8791 | 481.0523 | 483.362 | 485.7623 | 488.2523 | 490.8313 | 493.4985 | 496.2532 | 499.0948 | 502.0228 | 505.0366 | 508.1358 | 511.32 | 514.5888 | 517.942 | 521.3793 | 524.9006 | 528.5055 | 532.1941 | 535.9662 | 539.8218 | 543.7609 | 547.7835 | 551.8897 | 556.0796 | 560.3534 | 564.7111 | 569.1529 | 573.6792 | 578.2902 | 582.986 | 587.7672 | 592.6339 | 597.5866 | 602.6256 | 607.7514 | 612.9644 | 618.265
Washington Summer Peak (MW) | Segment | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064
Schedule 11 + Schedule 13 | General Service | 104.8596 | 115.2198 | 121.4124 | 122.5237 | 120.9913 | 120.6722 | 121.7066 | 122.7452 | 123.8647 | 124.596 | 125.3319 | 126.0724 | 126.8175 | 127.5673 | 128.3218 | 129.0811 | 129.8451 | 130.6138 | 131.3874 | 132.1658 | 132.949 | 133.7371 | 134.5302 | 135.3282 | 136.1311 | 136.9391 | 137.7521 | 138.5701 | 139.3932 | 140.2214 | 141.0548 | 141.8934 | 142.7371 | 143.5861 | 144.4403 | 145.2998 | 146.1647 | 147.0349 | 147.9105 | 148.7915 | 149.6779 | 150.5698 | 151.4673 | 152.3702 | 153.2788
Schedule 21 + Schedule 23 | Large General Service | 214.0322 | 222.2712 | 223.9596 | 219.5186 | 216.9837 | 214.0123 | 210.7496 | 206.7561 | 202.2606 | 198.7456 | 195.2939 | 191.9044 | 188.5758 | 185.3071 | 182.0969 | 178.9444 | 175.8483 | 172.8077 | 169.8214 | 166.8884 | 164.0078 | 161.1785 | 158.3996 | 155.6702 | 152.9893 | 150.356 | 147.7695 | 145.2288 | 142.7332 | 140.2817 | 137.8736 | 135.508 | 133.1842 | 130.9014 | 128.6588 | 126.4558 | 124.2915 | 122.1653 | 120.0764 | 118.0242 | 116.0081 | 114.0272 | 112.0811 | 110.169 | 108.2904
Schedule 25 | Extra Large General Service | 70.0973 | 72.5168 | 77.5923 | 77.9943 | 77.7645 | 77.0665 | 76.7313 | 76.5313 | 76.4257 | 76.1034 | 75.7856 | 75.4722 | 75.1634 | 74.8589 | 74.5587 | 74.2629 | 73.9714 | 73.6841 | 73.401 | 73.1221 | 72.8472 | 72.5765 | 72.3098 | 72.0471 | 71.7883 | 71.5335 | 71.2825 | 71.0354 | 70.7922 | 70.5527 | 70.3169 | 70.0849 | 69.8565 | 69.6318 | 69.4107 | 69.1931 | 68.9791 | 68.7686 | 68.5616 | 68.358 | 68.1578 | 67.961 | 67.7676 | 67.5775 | 67.3906
| C&I Total | 388.9892 | 410.0078 | 422.9642 | 420.0366 | 415.7394 | 411.751 | 409.1874 | 406.0326 | 402.551 | 399.445 | 396.4114 | 393.449 | 390.5567 | 387.7333 | 384.9775 | 382.2884 | 379.6648 | 377.1056 | 374.6097 | 372.1762 | 369.804 | 367.4921 | 365.2396 | 363.0454 | 360.9087 | 358.8286 | 356.8041 | 354.8344 | 352.9186 | 351.0558 | 349.2453 | 347.4863 | 345.7778 | 344.1193 | 342.5098 | 340.9488 | 339.4353 | 337.9688 | 336.5485 | 335.1737 | 333.8438 | 332.5581 | 331.316 | 330.1167 | 328.9598
| Residential Total | 499.1126 | 524.0413 | 544.774 | 540.5343 | 540.9934 | 551.6485 | 560.4949 | 570.5219 | 580.4872 | 588.839 | 597.311 | 605.9048 | 614.6223 | 623.4652 | 632.4353 | 641.5345 | 650.7646 | 660.1275 | 669.6251 | 679.2593 | 689.0322 | 698.9456 | 709.0018 | 719.2025 | 729.5501 | 740.0465 | 750.694 | 761.4946 | 772.4506 | 783.5643 | 794.8378 | 806.2736 | 817.8739 | 829.6411 | 841.5775 | 853.6858 | 865.9682 | 878.4273 | 891.0657 | 903.886 | 916.8907 | 930.0825 | 943.4641 | 957.0382 | 970.8076
| Total Res and C&I (Summer) | 888.1018 | 934.0491 | 967.7382 | 960.5709 | 956.7329 | 963.3995 | 969.6823 | 976.5545 | 983.0383 | 988.284 | 993.7223 | 999.3538 | 1005.179 | 1011.1984 | 1017.4128 | 1023.8229 | 1030.4294 | 1037.233 | 1044.2348 | 1051.4355 | 1058.8362 | 1066.4378 | 1074.2413 | 1082.248 | 1090.4588 | 1098.8751 | 1107.4981 | 1116.329 | 1125.3692 | 1134.6201 | 1144.0831 | 1153.7598 | 1163.6517 | 1173.7603 | 1184.0874 | 1194.6345 | 1205.4035 | 1216.3961 | 1227.6142 | 1239.0597 | 1250.7345 | 1262.6406 | 1274.78 | 1287.1549 | 1299.7674
Idaho Summer Peak (MW) | Segment | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064
Schedule 11 | General Service | 65.8743 | 72.3581 | 77.8131 | 82.7043 | 81.7944 | 83.0369 | 84.017 | 85.1934 | 86.3461 | 87.5235 | 88.717 | 89.9269 | 91.1535 | 92.3969 | 93.6574 | 94.9352 | 96.2306 | 97.5438 | 98.8751 | 100.2246 | 101.5927 | 102.9796 | 104.3856 | 105.8109 | 107.2558 | 108.7206 | 110.2054 | 111.7108 | 113.2368 | 114.7837 | 116.352 | 117.9418 | 119.5535 | 121.1873 | 122.8436 | 124.5227 | 126.2248 | 127.9504 | 129.6997 | 131.473 | 133.2708 | 135.0932 | 136.9407 | 138.8136 | 140.7123
Schedule 21 | Large General Service | 100.4406 | 100.4124 | 98.9002 | 97.7283 | 95.7656 | 94.1725 | 92.5668 | 90.5576 | 88.4514 | 86.7372 | 85.0654 | 83.4344 | 81.8429 | 80.2896 | 78.7733 | 77.2926 | 75.8465 | 74.4338 | 73.0536 | 71.7047 | 70.3861 | 69.0971 | 67.8366 | 66.6038 | 65.3979 | 64.2181 | 63.0636 | 61.9336 | 60.8276 | 59.7448 | 58.6845 | 57.6462 | 56.6292 | 55.6329 | 54.6569 | 53.7005 | 52.7633 | 51.8446 | 50.9442 | 50.0614 | 49.196 | 48.3473 | 47.515 | 46.6987 | 45.898
Schedule 25 | Extra Large General Service | 47.4638 | 49.4516 | 50.474 | 48.6482 | 49.8157 | 49.8301 | 49.8868 | 49.9255 | 49.9655 | 50.0034 | 50.0416 | 50.0799 | 50.1184 | 50.1572 | 50.1961 | 50.2352 | 50.2746 | 50.3141 | 50.3538 | 50.3938 | 50.4339 | 50.4743 | 50.5149 | 50.5556 | 50.5966 | 50.6378 | 50.6792 | 50.7208 | 50.7626 | 50.8047 | 50.8469 | 50.8894 | 50.9321 | 50.975 | 51.0181 | 51.0615 | 51.105 | 51.1488 | 51.1928 | 51.2371 | 51.2815 | 51.3262 | 51.3711 | 51.4163 | 51.4616
| C&I Total | 213.7786 | 222.222 | 227.1874 | 229.0808 | 227.3757 | 227.0395 | 226.4706 | 225.6766 | 224.763 | 224.2641 | 223.8239 | 223.4412 | 223.1148 | 222.8437 | 222.6268 | 222.4631 | 222.3517 | 222.2918 | 222.2825 | 222.3231 | 222.4128 | 222.551 | 222.7371 | 222.9703 | 223.2503 | 223.5764 | 223.9482 | 224.3652 | 224.827 | 225.3332 | 225.8834 | 226.4774 | 227.1147 | 227.7952 | 228.5186 | 229.2846 | 230.0931 | 230.9439 | 231.8367 | 232.7715 | 233.7482 | 234.7667 | 235.8268 | 236.9286 | 238.072
| Residential Total | 224.5151 | 235.9924 | 249.6839 | 250.5974 | 253.5858 | 256.555 | 258.7887 | 261.6122 | 264.8564 | 267.8043 | 270.7851 | 273.799 | 276.8464 | 279.9278 | 283.0435 | 286.1939 | 289.3793 | 292.6002 | 295.8569 | 299.1499 | 302.4795 | 305.8462 | 309.2503 | 312.6924 | 316.1728 | 319.6919 | 323.2501 | 326.848 | 330.4859 | 334.1643 | 337.8837 | 341.6444 | 345.447 | 349.2919 | 353.1797 | 357.1107 | 361.0854 | 365.1044 | 369.1681 | 373.2771 | 377.4318 | 381.6327 | 385.8804 | 390.1753 | 394.5181
| Total Res and C&I (Summer) | 438.2937 | 458.2144 | 476.8713 | 479.6782 | 480.9615 | 483.5945 | 485.2593 | 487.2888 | 489.6193 | 492.0684 | 494.609 | 497.2402 | 499.9613 | 502.7715 | 505.6703 | 508.6569 | 511.731 | 514.8919 | 518.1394 | 521.4729 | 524.8923 | 528.3972 | 531.9874 | 535.6627 | 539.4231 | 543.2683 | 547.1983 | 551.2132 | 555.3129 | 559.4975 | 563.7671 | 568.1218 | 572.5618 | 577.0872 | 581.6983 | 586.3953 | 591.1785 | 596.0483 | 601.0048 | 606.0486 | 611.18 | 616.3994 | 621.7072 | 627.104 | 632.5901
| Overall Winter System Peak | 1290.5988 | 1354.4917 | 1405.3721 | 1401.3152 | 1398.5938 | 1406.9301 | 1414.1126 | 1422.1553 | 1430.1079 | 1437.045 | 1444.257 | 1451.7434 | 1459.5037 | 1467.5378 | 1475.8455 | 1484.4268 | 1493.2816 | 1502.4103 | 1511.813 | 1521.4902 | 1531.4422 | 1541.6697 | 1552.1733 | 1562.9538 | 1574.012 | 1585.3488 | 1596.9653 | 1608.8625 | 1621.0416 | 1633.5039 | 1646.2507 | 1659.2835 | 1672.6037 | 1686.2131 | 1700.1131 | 1714.3056 | 1728.7924 | 1743.5754 | 1758.6565 | 1774.0378 | 1789.7215 | 1805.7096 | 1822.0045 | 1838.6086 | 1855.5242
| Overall Summer System Peak | 1326.3955 | 1392.2635 | 1444.6095 | 1440.2491 | 1437.6943 | 1446.994 | 1454.9416 | 1463.8433 | 1472.6576 | 1480.3524 | 1488.3313 | 1496.594 | 1505.1402 | 1513.9699 | 1523.0831 | 1532.4798 | 1542.1603 | 1552.125 | 1562.3742 | 1572.9085 | 1583.7285 | 1594.835 | 1606.2287 | 1617.9107 | 1629.8819 | 1642.1434 | 1654.6964 | 1667.5422 | 1680.6821 | 1694.1176 | 1707.8502 | 1721.8816 | 1736.2135 | 1750.8475 | 1765.7857 | 1781.0298 | 1796.582 | 1812.4444 | 1828.6191 | 1845.1083 | 1861.9145 | 1879.04 | 1896.4872 | 1914.2589 | 1932.3575
| Winter @ Generator | 1374.4877 | 1442.5337 | 1496.7213 | 1492.4007 | 1489.5023 | 1498.3805 | 1506.03 | 1514.5954 | 1523.065 | 1530.453 | 1538.1337 | 1546.1067 | 1554.3715 | 1562.9278 | 1571.7755 | 1580.9145 | 1590.345 | 1600.067 | 1610.0809 | 1620.387 | 1630.986 | 1641.8783 | 1653.0646 | 1664.5458 | 1676.3228 | 1688.3965 | 1700.768 | 1713.4385 | 1726.4093 | 1739.6816 | 1753.257 | 1767.1369 | 1781.323 | 1795.8169 | 1810.6205 | 1825.7355 | 1841.1639 | 1856.9078 | 1872.9692 | 1889.3503 | 1906.0534 | 1923.0807 | 1940.4348 | 1958.1182 | 1976.1333
| Summer @ Generator | 1412.6112 | 1482.7607 | 1538.5091 | 1533.8653 | 1531.1445 | 1541.0487 | 1549.5128 | 1558.9931 | 1568.3804 | 1576.5753 | 1585.0728 | 1593.8726 | 1602.9743 | 1612.378 | 1622.0835 | 1632.091 | 1642.4007 | 1653.0131 | 1663.9285 | 1675.1475 | 1686.6709 | 1698.4993 | 1710.6336 | 1723.0749 | 1735.8242 | 1748.8827 | 1762.2516 | 1775.9324 | 1789.9264 | 1804.2352 | 1818.8605 | 1833.8039 | 1849.0673 | 1864.6526 | 1880.5617 | 1896.7968 | 1913.3599 | 1930.2533 | 1947.4793 | 1965.0404 | 1982.9389 | 2001.1776 | 2019.7589 | 2038.6857 | 2057.9608
|  |  |  | 0.4968% | 9.935%
|  |  |  | 0.5302% | 10.6%
| Updated: 4/18/2024 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064
Energy (kWh) | WA Residential | 2533874444.5088 | 2654411233.768 | 2755431191.2021 | 2733819062.364 | 2736141127.1787 | 2790030412.605 | 2834772090.3439 | 2885484904.4706 | 2935885928.1868 | 2978126080.8549 | 3020973965.0701 | 3064438324.5895 | 3108528028.9714 | 3153252075.3848 | 3198619590.446 | 3244639832.0808 | 3291322191.4137 | 3338676194.6842 | 3386711505.1909 | 3435437925.2634 | 3484865398.2628 | 3535004010.6104 | 3585863993.8464 | 3637455726.7175 | 3689789737.2949 | 3742876705.1229 | 3796727463.398 | 3851353001.1797 | 3906764465.6329 | 3962973164.3028 | 4019990567.422 | 4077828310.2518 | 4136498195.4559 | 4196012195.5094 | 4256382455.1417 | 4317621293.8147 | 4379741208.2374 | 4442754874.9151 | 4506675152.737 | 4571515085.5999 | 4637287905.0702 | 4704007033.0838 | 4771686084.685 | 4840338870.8052 | 4909979401.0809
| ID Residential | 1249251618.5443 | 1310008276.9946 | 1381843116.7202 | 1386880287.7883 | 1403418695.0774 | 1419851260.3297 | 1432212987.9684 | 1447839409.5637 | 1465793507.1574 | 1482108229.7661 | 1498604540.1445 | 1515284459.4191 | 1532150031.2121 | 1549203321.892 | 1566446420.8263 | 1583881440.638 | 1601510517.4642 | 1619335811.218 | 1637359505.8526 | 1655583809.6295 | 1674010955.3889 | 1692643200.823 | 1711482828.753 | 1730532147.4083 | 1749793490.7097 | 1769269218.5555 | 1788961717.11 | 1808873399.0964 | 1829006704.0922 | 1849364098.8283 | 1869948077.4907 | 1890761162.0268 | 1911805902.4539 | 1933084877.1716 | 1954600693.2782 | 1976355986.8894 | 1998353423.462 | 2020595698.1198 | 2043085535.9846 | 2065825692.5092 | 2088818953.8155 | 2112068137.036 | 2135576090.6586 | 2159345694.8755 | 2183379861.9367
Customer | WA Residential | 232273.5 | 235525.4167 | 238456.1389 | 241043.25 | 243967.7385 | 247329.6451 | 250634.9737 | 254016.4432 | 257194.8586 | 260552.8495 | 263954.6831 | 267400.9317 | 270892.1753 | 274429.0013 | 278012.0048 | 281641.7888 | 285318.9641 | 289044.1493 | 292817.9714 | 296641.0652 | 300514.0742 | 304437.6501 | 308412.4529 | 312439.1517 | 316518.4239 | 320650.9559 | 324837.4431 | 329078.5901 | 333375.1103 | 337727.7268 | 342137.172 | 346604.1879 | 351129.5261 | 355713.9481 | 360358.2252 | 365063.139 | 369829.4812 | 374658.0538 | 379549.6692 | 384505.1506 | 389525.3319 | 394611.0576 | 399763.1838 | 404982.5771 | 410270.116
| ID Residential | 118386.0833 | 121023.7917 | 123064.0417 | 124910.875 | 126857.2626 | 128866.8631 | 130882.6905 | 132911.4405 | 134923.3571 | 137020.1781 | 139149.5853 | 141312.0853 | 143508.1924 | 145738.4288 | 148003.3249 | 150303.4193 | 152639.2592 | 155011.3999 | 157420.4057 | 159866.8494 | 162351.3129 | 164874.387 | 167436.6718 | 170038.7766 | 172681.3203 | 175364.9313 | 178090.2478 | 180857.918 | 183668.6001 | 186522.9626 | 189421.6842 | 192365.4543 | 195354.9731 | 198390.9515 | 201474.1115 | 204605.1863 | 207784.9207 | 211014.0708 | 214293.4045 | 217623.7018 | 221005.7547 | 224440.3675 | 227928.357 | 231470.5528 | 235067.7973
WA | Avg. Annual Growth | 2020: 1.426%; 2021: 4.757%; 0.5302% 2022: 3.806%; 10.6% 2023: -0.7843%; 10.6% 2024: 0.08494%; 10.6% 2025: 1.97%; 10.6% 2026: 1.604%; 10.6% 2027: 1.789%; 10.6% 2028: 1.747%; 10.6% 2029: 1.439%
ID | Avg. Annual Growth | 2020: 1.107%; 2021: 4.863%; 0.5302% 2022: 5.484%; 10.6% 2023: 0.3645%; 10.6% 2024: 1.192%; 10.6% 2025: 1.171%; 10.6% 2026: 0.8706%; 10.6% 2027: 1.091%; 10.6% 2028: 1.24%; 10.6% 2029: 1.113%
WA | Avg. Annual Growth | 2020: 1.297%; 2021: 1.4%; 0.5302% 2022: 1.244%; 10.6% 2023: 1.085%; 10.6% 2024: 1.213%; 10.6% 2025: 1.378%; 10.6% 2026: 1.336%; 10.6% 2027: 1.349%; 10.6% 2028: 1.251%; 10.6% 2029: 1.306%
ID | Avg. Annual Growth | 2020: 1.542%; 2021: 2.228%; 0.5302% 2022: 1.686%; 10.6% 2023: 1.501%; 10.6% 2024: 1.558%; 10.6% 2025: 1.584%; 10.6% 2026: 1.564%; 10.6% 2027: 1.55%; 10.6% 2028: 1.514%; 10.6% 2029: 1.554%
Res Load Factor (W)
| Washington | 2020: 0.6131
| Idaho | 2020: 0.63256
|  |  | Washington Shares | Idaho Shares
| For Cost Allocation: | 2020: Residential; 2021: 64.81%; 0.5302% 2022: 57.09%
| Share of 2039 demand potential | 2020: General Service; 2021: 12.95%; 0.5302% 2022: 20.51%
|  | Large General Service | 14.56% | 12.51%
|  | Extra Large General Service | 7.681% | 9.897%
Max Demand @ Meter
Source: "F:\AEG\Clients\Avista Energy\1008250 CPA 2023\LoadMAP\Avista Electric Forecast - Hourly WIP v3.xlsb"
|  | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047
| Washington | [27 empty] | Commercial | Industrial
Summer | Residential Max Summer Peak | 494.7399 | 568.4726 | 575.13 | 542.8755 | 552.8135 | 561.7595 | 571.5206 | 577.0885 | 588.7616 | 603.222 | 616.4266 | 624.8491 | 638.561 | 649.6658 | 667.5186 | 691.3185 | 705.1523 | 725.699 | 748.3617 | 765.8965 | 794.6105 | 819.8526 | 841.6822 | 860.9604 | 895.7177 | 918.7502 | 952.7709
| Commercial Max Summer Peak | 518.3443 | 506.9895 | 499.0148 | 466.4577 | 466.75 | 462.2149 | 456.6938 | 446.3603 | 453.8045 | 460.2 | 464.7388 | 467.4302 | 471.2372 | 475.4798 | 482.7448 | 492.1317 | 495.1674 | 501.9879 | 510.2228 | 515.2419 | 527.2765 | 538.1552 | 548.319 | 559.232 | 579.8662 | 572.2074 | 593.1927
| General Service Max Summer Peak | 148.8499 | 150.1083 | 150.3588 | 140.3214 | 141.057 | 141.5929 | 142.1247 | 141.4099 | 143.7532 | 145.7601 | 147.1772 | 148.0149 | 149.1893 | 150.5107 | 152.7829 | 155.7185 | 156.6648 | 158.7887 | 161.3608 | 162.9116 | 166.6998 | 170.0997 | 173.2672 | 176.6666 | 183.1182 | 180.7263 | 187.2953 | 31.26% | 1.185%
| Large GS Max Summer Peak | 335.229 | 324.0368 | 316.0926 | 296.8167 | 295.3461 | 289.5686 | 282.7855 | 273.1072 | 277.4161 | 281.0167 | 283.4544 | 284.8586 | 286.6723 | 288.8974 | 292.8651 | 297.9862 | 299.5916 | 303.1651 | 307.6049 | 310.0358 | 317.0017 | 322.8999 | 328.2649 | 333.999 | 345.2323 | 341.1071 | 352.6563 | 54.34% | 19.3%
| Extra Large GS Max Summer Peak | 184.4987 | 192.0454 | 197.1203 | 191.6522 | 192.631 | 191.7731 | 191.0087 | 190.0604 | 192.217 | 193.6526 | 194.1871 | 194.3336 | 193.8301 | 194.1089 | 195.2351 | 196.6678 | 196.9223 | 197.3555 | 198.3949 | 197.895 | 201.3816 | 202.8905 | 203.7003 | 204.4615 | 207.5129 | 206.5626 | 210.18 | 14.39% | 79.52%
| Industrial Max Summer Peak | 150.2334 | 159.201 | 164.557 | 162.3326 | 162.2841 | 160.7198 | 159.2251 | 158.2172 | 159.5817 | 160.2294 | 160.0799 | 159.7769 | 158.4546 | 158.0371 | 158.1382 | 158.2408 | 158.0113 | 157.3213 | 157.1378 | 155.6005 | 157.8067 | 157.7349 | 156.9134 | 155.8951 | 155.9972 | 156.1885 | 156.9389
Winter | Residential Max Winter Peak | 659.2265 | 659.4995 | 652.9161 | 652.1631 | 664.4622 | 678.0983 | 701.4242 | 709.5888 | 702.9109 | 701.2251 | 701.0844 | 705.9777 | 715.1122 | 719.9721 | 728.9307 | 735.9391 | 750.4915 | 773.8718 | 783.2843 | 797.009 | 809.7171 | 824.5275 | 844.7551 | 877.345 | 894.9433 | 905.0032 | 921.286
| Commercial Max Winter Peak | 360.1385 | 375.9114 | 367.2605 | 364.1604 | 363.8042 | 363.1646 | 364.928 | 359.6277 | 362.3005 | 364.3473 | 366.3477 | 367.4359 | 377.0016 | 380.9457 | 384.6248 | 387.7468 | 391.9405 | 399.8396 | 403.3644 | 406.5158 | 417.9484 | 427.4746 | 440.2261 | 456.1904 | 454.7218 | 463.1938 | 479.9929
| General Service Max Winter Peak | 103.3136 | 111.0995 | 110.4568 | 109.2581 | 109.6598 | 110.9523 | 113.2459 | 113.5986 | 114.4403 | 115.0822 | 115.7056 | 116.0424 | 119.0277 | 120.2579 | 121.4074 | 122.3822 | 123.6919 | 126.1584 | 127.259 | 128.2354 | 131.8197 | 134.7966 | 138.7783 | 143.7628 | 143.3059 | 145.9544 | 151.2091 | 31.26% | 1.185%
| Large GS Max Winter Peak | 231.0916 | 236.5575 | 229.0408 | 226.6326 | 225.0988 | 222.3491 | 220.5687 | 214.605 | 216.1586 | 217.3037 | 218.3591 | 218.8957 | 224.0131 | 226.1124 | 228.1007 | 229.7795 | 232.0369 | 236.2852 | 238.1801 | 239.7496 | 246.1327 | 251.2922 | 258.1491 | 266.7264 | 265.9637 | 270.5697 | 279.7514 | 54.34% | 19.3%
| Extra Large GS Max Winter Peak | 122.1475 | 129.1668 | 131.3097 | 130.2508 | 130.5587 | 130.4768 | 131.014 | 130.7374 | 131.5387 | 131.9684 | 132.1258 | 132.0567 | 133.0996 | 133.4855 | 133.9693 | 134.3451 | 134.8598 | 135.8135 | 136.2359 | 136.0997 | 138.4463 | 139.7453 | 141.2805 | 143.1729 | 143.1074 | 144.3347 | 146.968 | 14.39% | 79.52%
| Industrial Max Winter Peak | 96.4142 | 100.9123 | 103.5469 | 101.9812 | 101.5131 | 100.6135 | 99.9006 | 99.3133 | 99.8372 | 100.007 | 99.8428 | 99.5589 | 99.1389 | 98.9102 | 98.8526 | 98.76 | 98.6481 | 98.4175 | 98.3107 | 97.5689 | 98.4504 | 98.3594 | 97.9817 | 97.4716 | 97.6551 | 97.6649 | 97.9355
Idaho
Summer | Residential Max Summer Peak | 228.9292 | 247.6565 | 250.4979 | 234.2244 | 238.242 | 242.2429 | 247.1678 | 252.8497 | 256.1868 | 263.2499 | 269.9867 | 277.1878 | 282.3368 | 288.6995 | 297.6395 | 308.844 | 316.536 | 326.8924 | 338.0342 | 347.106 | 360.8584 | 373.2415 | 384.3939 | 394.5618 | 411.6365 | 423.1005 | 439.354
| Commercial Max Summer Peak | 223.9141 | 214.9487 | 220.225 | 208.8502 | 210.3885 | 208.8441 | 207.7014 | 203.9604 | 207.0622 | 209.2694 | 210.7374 | 210.7283 | 212.0714 | 212.9008 | 214.8039 | 217.5654 | 217.9379 | 220.1212 | 223.2148 | 225.1567 | 230.0631 | 234.8395 | 239.0845 | 243.1464 | 252.2924 | 248.3408 | 256.9547
| General Service Max Summer Peak | 93.6189 | 94.6411 | 106.003 | 111.0204 | 113.8868 | 116.4926 | 119.4606 | 121.0489 | 122.8499 | 124.1199 | 124.9487 | 124.9169 | 125.6578 | 126.1128 | 127.199 | 128.7838 | 128.9766 | 130.2159 | 131.9913 | 133.0795 | 135.9409 | 138.6966 | 141.1342 | 143.4631 | 148.7622 | 146.4505 | 151.4482 | 58.11% | 2.335%
| Large GS Max Summer Peak | 136.8701 | 126.957 | 124.0466 | 106.3109 | 103.3632 | 98.239 | 92.9357 | 86.2245 | 87.3413 | 88.0799 | 88.4937 | 88.3609 | 88.6547 | 88.8239 | 89.4173 | 90.3209 | 90.3411 | 90.9888 | 92.0009 | 92.5084 | 94.3366 | 95.9706 | 97.3667 | 98.685 | 101.9232 | 100.4165 | 103.4995 | 36.24% | 11.38%
| Extra Large GS Max Summer Peak | 106.2696 | 103.9952 | 100.9425 | 101.7952 | 104.1105 | 104.5487 | 104.8082 | 104.8232 | 104.9419 | 104.6011 | 103.7868 | 102.8045 | 101.4165 | 100.4667 | 99.8437 | 99.262 | 98.4119 | 97.4466 | 96.7935 | 95.4138 | 96.0696 | 95.603 | 94.7622 | 93.825 | 93.7602 | 92.9721 | 93.1628 | 5.645% | 86.29%
| Industrial Max Summer Peak | 112.8446 | 110.6446 | 110.7671 | 110.2763 | 110.972 | 110.4362 | 109.503 | 108.1363 | 108.0709 | 107.5316 | 106.4918 | 105.354 | 103.6576 | 102.5026 | 101.656 | 100.8013 | 99.7917 | 98.5302 | 97.5708 | 95.8449 | 96.2839 | 95.4307 | 94.1786 | 92.8266 | 92.1531 | 91.4984 | 91.1559
Winter | Residential Max Winter Peak | 309.5841 | 322.8133 | 322.1897 | 319.0506 | 322.1928 | 326.4841 | 334.9027 | 338.3439 | 338.6072 | 340.7979 | 344.4542 | 349.9447 | 358.0139 | 363.6593 | 369.9858 | 375.2319 | 383.4596 | 395.9398 | 401.7961 | 409.4127 | 416.6637 | 424.7677 | 435.7158 | 452.8762 | 462.9631 | 469.9204 | 479.1609
| Commercial Max Winter Peak | 160.7856 | 169.6879 | 169.3593 | 168.8365 | 169.0844 | 168.9072 | 169.979 | 167.9308 | 169.0048 | 169.4436 | 169.9376 | 169.6476 | 173.1322 | 174.1503 | 175.0631 | 175.8278 | 177.2143 | 179.9392 | 181.0785 | 182.0232 | 183.6437 | 186.5037 | 191.7948 | 198.1027 | 198.386 | 200.7456 | 207.8025
| General Service Max Winter Peak | 67.0834 | 74.4445 | 81.2512 | 89.344 | 91.119 | 93.7923 | 97.3182 | 99.2096 | 99.8283 | 100.0722 | 100.3432 | 100.1569 | 102.1628 | 102.7382 | 103.2548 | 103.6849 | 104.4765 | 106.0445 | 106.693 | 107.2195 | 108.1618 | 109.8109 | 112.8692 | 116.5167 | 116.6733 | 118.0337 | 122.1274 | 58.11% | 2.335%
| Large GS Max Winter Peak | 96.7516 | 97.598 | 92.9 | 83.032 | 80.4708 | 76.9399 | 73.6184 | 68.7708 | 69.1335 | 69.2387 | 69.3393 | 69.1473 | 70.3176 | 70.6073 | 70.8709 | 71.0781 | 71.5122 | 72.4243 | 72.7709 | 73.0042 | 73.5943 | 74.5682 | 76.4056 | 78.6035 | 78.667 | 79.4697 | 81.9925 | 36.24% | 11.38%
| Extra Large GS Max Winter Peak | 69.0394 | 68.8375 | 66.4101 | 67.2635 | 68.5374 | 68.9038 | 69.2912 | 69.4527 | 69.3114 | 68.9279 | 68.361 | 67.6859 | 67.1799 | 66.6359 | 66.1775 | 65.6904 | 65.25 | 64.8313 | 64.3923 | 63.6179 | 63.7308 | 63.4171 | 63.107 | 62.7936 | 62.5121 | 62.2478 | 62.3813 | 5.645% | 86.29%
| Industrial Max Winter Peak | 72.0887 | 71.1921 | 71.2019 | 70.803 | 71.0429 | 70.7288 | 70.2488 | 69.5024 | 69.2684 | 68.7952 | 68.1059 | 67.3425 | 66.5281 | 65.831 | 65.2401 | 64.6255 | 64.0244 | 63.361 | 62.7777 | 61.8184 | 61.8432 | 61.2925 | 60.5871 | 59.8111 | 59.4664 | 59.0057 | 58.6987
WA Usage
| Class 11 | 2021: Class 21; 2022: Class 25; 2023: Pumping; 2025: *Combined in Class 11; 2030: WA Commercial breakout
| WASCH11KWH.c | WASCH21KWH.c | WASCH25KWH.c | WASCH31KWH.c | WASCH47KWH.c (No Customer Count) | WASCH13KWH.c | WASCH23KWH.c | WATOTALKWH.c | WA Total for LoadMAP |  | GS | LGS | ELGS |  | Commercial Summer | GS | LGS | ELGS |  | Commercial Winter | GS | LGS | ELGS
| 580916093.3995 | 1190145022.0412 | 279253091.768 | 79204174.7012 | 4118359.6902 | 38901.37 | 87569.75 | 2133763212.7202 | 2050440678.3287 | 2021 | 28.33% | 58.05% | 13.62% |  | 518.3443 | 146.8634 | 300.8867 | 70.5942 |  | 360.1385 | 102.0387 | 209.0519 | 49.0479
| 612468857.47 | 1196634299.2936 | 285594158.506 | 70033084.0165 | 3953015.6438 | 189126.39 | 247554.31 | 2169120095.6299 | 2095133995.9696 | 2022 | 29.24% | 57.13% | 13.63% |  | 506.9895 | 148.2536 | 289.6266 | 69.1093 |  | 375.9114 | 109.9238 | 214.746 | 51.2416
| 617908656.5631 | 1175301966.133 | 283828835.191 | 72919501.1472 | 3827731.3742 | 445047.02 | 1016251.47 | 2155247988.8985 | 2078500756.3771 | 2023 | 29.75% | 56.59% | 13.66% |  | 499.0148 | 148.4568 | 282.4152 | 68.1428 |  | 367.2605 | 109.2599 | 207.8494 | 50.1511
| 609924604.2924 | 1159462137.35 | 284952440.55 | 73866445.75 | 3679342.8254 | 602987.3769 | 2447813.9595 | 2134935772.1042 | 2057389983.5288 | 2024 | 29.67% | 56.47% | 13.85% |  | 466.4577 | 138.4207 | 263.4318 | 64.6053 |  | 364.1604 | 108.0641 | 205.6594 | 50.4369
| 608524515 | 1144925154 | 286093360 | 72867199.962 | 3538713.0998 | 602642.6514 | 2315283.029 | 2118866867.7421 | 2042460954.6804 | 2025 | 29.82% | 56.17% | 14.01% |  | 466.75 | 139.1998 | 262.1712 | 65.379 |  | 363.8042 | 108.4981 | 204.3471 | 50.9591
| 613786983 | 1128682539 | 287014030 | 74923646.3466 | 3394203.9626 | 603576.8977 | 2313167.5732 | 2110718146.7801 | 2032400296.4709 | 2026 | 30.23% | 55.65% | 14.12% |  | 462.2149 | 139.7266 | 257.2146 | 65.2736 |  | 363.1646 | 109.7839 | 202.0949 | 51.2858
| 619071629 | 1108218345.25 | 287562790 | 74175463.9067 | 3251634.5312 | 603499.7491 | 2313450.0169 | 2095196812.4539 | 2017769714.016 | 2027 | 30.71% | 55.04% | 14.25% |  | 456.6938 | 140.2548 | 251.3533 | 65.0858 |  | 364.928 | 112.0726 | 200.8476 | 52.0078
| 624768066 | 1084863901.75 | 287967900 | 74696553.0746 | 3108095.2469 | 603505.4499 | 2313432.4095 | 2078321453.9308 | 2000516805.6094 | 2028 | 31.26% | 54.34% | 14.39% |  | 446.3603 | 139.5345 | 242.5737 | 64.2521 |  | 359.6277 | 112.4214 | 195.439 | 51.7672
[11 empty] | 31.26% | 54.34% | 14.39%
WA Industrial breakout
| Year | 2021: WASCH11KWH.i; 2022: WASCH21KWH.i; 2023: WASCH25KWH.i (Excluding IEP); 2034: Industrial Summer; 2035: GS; 2036: LGS; 2037: ELGS; 2039: Industrial Winter; 2040: GS; 2041: LGS; 2042: ELGS
| 2021 Actual | 2021: 5292386.4616; 2022: 91492005.9801; 2023: 303454290.8877; 2024: 400238683.3295; 2029: 2021; 2030: 1.322%; 2031: 22.86%; 2032: 75.82%; 2034: 150.2334; 2035: 1.9865; 2036: 34.3424; 2037: 113.9044; 2039: 96.4142; 2040: 1.2749; 2041: 22.0397; 2042: 73.0996
| 2022 Actual | 2021: 5097825.1198; 2022: 94578563.858; 2023: 337897395.449; 2024: 437573784.4268; 2029: 2022; 2030: 1.165%; 2031: 21.61%; 2032: 77.22%; 2034: 159.201; 2035: 1.8547; 2036: 34.4102; 2037: 122.9361; 2039: 100.9123; 2040: 1.1756; 2041: 21.8115; 2042: 77.9251
| 2023 Actual | 2021: 5056586.13; 2022: 89533210.6401; 2023: 342893243.155; 2024: 437483039.9251; 2029: 2023; 2030: 1.156%; 2031: 20.47%; 2032: 78.38%; 2034: 164.557; 2035: 1.902; 2036: 33.6775; 2037: 128.9775; 2039: 103.5469; 2040: 1.1968; 2041: 21.1914; 2042: 81.1586
| 2024 Forecast | 2021: 5085425.8257; 2022: 89323870.4367; 2023: 339923222.7; 2024: 434332518.9624; 2029: 2024; 2030: 1.171%; 2031: 20.57%; 2032: 78.26%; 2034: 162.3326; 2035: 1.9007; 2036: 33.385; 2037: 127.047; 2039: 101.9812; 2040: 1.1941; 2041: 20.9732; 2042: 79.8139
| 2025 Forecast | 2021: 4862651.146; 2022: 86858927.2267; 2023: 333173665; 2024: 424895243.3727; 2029: 2025; 2030: 1.144%; 2031: 20.44%; 2032: 78.41%; 2034: 162.2841; 2035: 1.8572; 2036: 33.1748; 2037: 127.252; 2039: 101.5131; 2040: 1.1618; 2041: 20.7517; 2042: 79.5996
| 2026 Forecast | 2021: 4862041.9462; 2022: 84289405.2667; 2023: 329558911; 2024: 418710358.2128; 2029: 2026; 2030: 1.161%; 2031: 20.13%; 2032: 78.71%; 2034: 160.7198; 2035: 1.8663; 2036: 32.354; 2037: 126.4994; 2039: 100.6135; 2040: 1.1683; 2041: 20.2542; 2042: 79.1909
| 2027 Forecast | 2021: 4861888.571; 2022: 81724920.92; 2023: 327403571; 2024: 413990380.491; 2029: 2027; 2030: 1.174%; 2031: 19.74%; 2032: 79.08%; 2034: 159.2251; 2035: 1.8699; 2036: 31.4323; 2037: 125.9229; 2039: 99.9006; 2040: 1.1732; 2041: 19.7212; 2042: 79.0062
| 2028 Forecast | 2021: 4861873.1859; 2022: 79156090.44; 2023: 326149846; 2024: 410167809.6259; 2029: 2028; 2030: 1.185%; 2031: 19.3%; 2032: 79.52%; 2034: 158.2172; 2035: 1.8754; 2036: 30.5335; 2037: 125.8083; 2039: 99.3133; 2040: 1.1772; 2041: 19.1659; 2042: 78.9702
[11 empty] | 1.185% | 19.3% | 79.52% |  | Total | 148.8499 | 335.229 | 184.4987 |  |  | 103.3136 | 231.0916 | 122.1475
[16 empty] | 150.1083 | 324.0368 | 192.0454 |  |  | 111.0995 | 236.5575 | 129.1668
[16 empty] | 150.3588 | 316.0926 | 197.1203 |  |  | 110.4568 | 229.0408 | 131.3097
[16 empty] | 140.3214 | 296.8167 | 191.6522 |  |  | 109.2581 | 226.6326 | 130.2508
[16 empty] | 141.057 | 295.3461 | 192.631 |  |  | 109.6598 | 225.0988 | 130.5587
[16 empty] | 141.5929 | 289.5686 | 191.7731 |  |  | 110.9523 | 222.3491 | 130.4768
| ID Usage | 2035: 142.1247; 2036: 282.7855; 2037: 191.0087; 2040: 113.2459; 2041: 220.5687; 2042: 131.014
[16 empty] | 141.4099 | 273.1072 | 190.0604 |  |  | 113.5986 | 214.605 | 130.7374
| Class 11 | 2021: Class 21; 2022: Class 25; 2023: Pumping; 2024: *Combined in Class 21; 2030: ID Commercial breakout
| IDSCH11KWH.c | IDSCH21KWH.c | IDSCH25KWH.c | IDSCH31KWH.c | IDSCH48KWH.c | IDSCH49KWH.c | IDSCH47KWH.c, IDSCH49KWH.c | IDTOTALKWH.c | ID Total for LoadMAP |  | GS | LGS | ELGS |  | Commercial Summer | GS | LGS | ELGS |  | Commercial Winter | GS | LGS | ELGS
| 399763959.9423 | 511727664.9189 | 63232142.6037 | 43582323.5898 | 376175.782 | 2161306.653 | 2537482.435 | 1020843573.4896 | 974723767.4648 | 2021 | 41.01% | 52.5% | 6.487% |  | 223.9141 | 91.834 | 117.5544 | 14.5257 |  | 160.7856 | 65.9431 | 84.4121 | 10.4305
| 429904049.9639 | 504797085.2332 | 61039672.883 | 41447879.2412 | 342528.47 | 2121928.857 | 2464457.327 | 1039653144.6483 | 995740808.0801 | 2022 | 43.17% | 50.7% | 6.13% |  | 214.9487 | 92.8026 | 108.9696 | 13.1765 |  | 169.6879 | 73.2616 | 86.0244 | 10.402
| 472274520.2102 | 474083224.0023 | 54873923.409 | 43090251.2795 | 316963.4445 | 2041369.259 | 2358332.7035 | 1046680251.6045 | 1001231667.6215 | 2023 | 47.17% | 47.35% | 5.481% |  | 220.225 | 103.8787 | 104.2766 | 12.0697 |  | 169.3593 | 79.8857 | 80.1916 | 9.282
| 542070750.262 | 443390013.2 | 57192687.6 | 42014318.2569 | 312594.7684 | 2055820.882 | 2368415.6504 | 1087036184.9693 | 1042653451.062 | 2024 | 51.99% | 42.53% | 5.485% |  | 208.8502 | 108.5802 | 88.8139 | 11.4561 |  | 168.8365 | 87.7773 | 71.798 | 9.2612
| 546746946 | 429320570 | 56662407 | 42079214.8874 | 286625.395 | 1983831.0705 | 2270456.4655 | 1077079594.3529 | 1032729923 | 2025 | 52.94% | 41.57% | 5.487% |  | 210.3885 | 111.3837 | 87.4615 | 11.5433 |  | 169.0844 | 89.5165 | 70.2908 | 9.2771
| 552294760 | 403691930 | 56013942 | 41958518.6144 | 260348.1042 | 1955061.9762 | 2215410.0805 | 1056174560.6949 | 1012000632 | 2026 | 54.57% | 39.89% | 5.535% |  | 208.8441 | 113.9757 | 83.3089 | 11.5595 |  | 168.9072 | 92.1803 | 67.3779 | 9.349
| 558574431 | 378063290 | 55482231 | 41799010.2112 | 234068.107 | 1904682.5234 | 2138750.6304 | 1036057712.8415 | 992119952 | 2027 | 56.3% | 38.11% | 5.592% |  | 207.7014 | 116.9382 | 79.148 | 11.6153 |  | 169.979 | 95.7 | 64.7732 | 9.5057
| 565085175 | 352434650 | 54896511 | 41889769.4479 | 207788.107 | 1865108.2498 | 2072896.3568 | 1016379001.8047 | 972416336 | 2028 | 58.11% | 36.24% | 5.645% |  | 203.9604 | 118.5243 | 73.9217 | 11.5143 |  | 167.9308 | 97.587 | 60.8635 | 9.4803
[11 empty] | 58.11% | 36.24% | 5.645%
ID Industrial breakout
| Year | 2021: IDSCH11KWH.i; 2022: IDSCH21KWH.i; 2023: IDSCH25KWH.i; 2034: Industrial Summer; 2035: GS; 2036: LGS; 2037: ELGS; 2039: Industrial Winter; 2040: GS; 2041: LGS; 2042: ELGS
| 2021 Actual | 2021: 5478416.0733; 2022: 59284937.137; 2023: 281585393.3203; 2024: 346348746.5307; 2029: 2021; 2030: 1.582%; 2031: 17.12%; 2032: 81.3%; 2034: 112.8446; 2035: 1.7849; 2036: 19.3157; 2037: 91.7439; 2039: 72.0887; 2040: 1.1403; 2041: 12.3395; 2042: 58.6089
| 2022 Actual | 2021: 5889201.6449; 2022: 57616569.2291; 2023: 290907205.873; 2024: 354412976.747; 2029: 2022; 2030: 1.662%; 2031: 16.26%; 2032: 82.08%; 2034: 110.6446; 2035: 1.8386; 2036: 17.9874; 2037: 90.8186; 2039: 71.1921; 2040: 1.183; 2041: 11.5736; 2042: 58.4355
| 2023 Actual | 2021: 6586687.1046; 2022: 61300984.0034; 2023: 275567599.489; 2024: 343455270.597; 2029: 2023; 2030: 1.918%; 2031: 17.85%; 2032: 80.23%; 2034: 110.7671; 2035: 2.1243; 2036: 19.7701; 2037: 88.8728; 2039: 71.2019; 2040: 1.3655; 2041: 12.7083; 2042: 57.1281
| 2024 Forecast | 2021: 7788105.1267; 2022: 55845182.5667; 2023: 288333909.17; 2024: 351967196.8633; 2029: 2024; 2030: 2.213%; 2031: 15.87%; 2032: 81.92%; 2034: 110.2763; 2035: 2.4401; 2036: 17.4971; 2037: 90.3391; 2039: 70.803; 2040: 1.5667; 2041: 11.234; 2042: 58.0023
| 2025 Forecast | 2021: 7768789.2667; 2022: 49353515.2733; 2023: 287298039; 2024: 344420343.54; 2029: 2025; 2030: 2.256%; 2031: 14.33%; 2032: 83.41%; 2034: 110.972; 2035: 2.5031; 2036: 15.9017; 2037: 92.5672; 2039: 71.0429; 2040: 1.6025; 2041: 10.18; 2042: 59.2604
| 2026 Forecast | 2021: 7775119.3067; 2022: 46121625.2; 2023: 287259189; 2024: 341155933.5067; 2029: 2026; 2030: 2.279%; 2031: 13.52%; 2032: 84.2%; 2034: 110.4362; 2035: 2.5169; 2036: 14.9301; 2037: 92.9892; 2039: 70.7288; 2040: 1.6119; 2041: 9.562; 2042: 59.5549
| 2027 Forecast | 2021: 7774934.4; 2022: 42498044.8533; 2023: 287249704; 2024: 337522683.2533; 2029: 2027; 2030: 2.304%; 2031: 12.59%; 2032: 85.11%; 2034: 109.503; 2035: 2.5224; 2036: 13.7877; 2037: 93.1929; 2039: 70.2488; 2040: 1.6182; 2041: 8.8451; 2042: 59.7854
| 2028 Forecast | 2021: 7771959.8267; 2022: 37874387.5067; 2023: 287253022; 2024: 332899369.3333; 2029: 2028; 2030: 2.335%; 2031: 11.38%; 2032: 86.29%; 2034: 108.1363; 2035: 2.5246; 2036: 12.3028; 2037: 93.3089; 2039: 69.5024; 2040: 1.6226; 2041: 7.9074; 2042: 59.9724
[11 empty] | 2.335% | 11.38% | 86.29% |  | Total | 93.6189 | 136.8701 | 106.2696 |  |  | 67.0834 | 96.7516 | 69.0394
[16 empty] | 94.6411 | 126.957 | 103.9952 |  |  | 74.4445 | 97.598 | 68.8375
[16 empty] | 106.003 | 124.0466 | 100.9425 |  |  | 81.2512 | 92.9 | 66.4101
[16 empty] | 111.0204 | 106.3109 | 101.7952 |  |  | 89.344 | 83.032 | 67.2635
[16 empty] | 113.8868 | 103.3632 | 104.1105 |  |  | 91.119 | 80.4708 | 68.5374
[16 empty] | 116.4926 | 98.239 | 104.5487 |  |  | 93.7923 | 76.9399 | 68.9038
[16 empty] | 119.4606 | 92.9357 | 104.8082 |  |  | 97.3182 | 73.6184 | 69.2912
[16 empty] | 121.0489 | 86.2245 | 104.8232 |  |  | 99.2096 | 68.7708 | 69.4527
Note on O9: Forsyth, Grant: Avg. of Jan-Mar due to missing customers over this period.
Note on Q9: Forsyth, Grant: Avg. of Jan-Mar due to missing customers over this period.
Note on C27: Forsyth, Grant: Avg. of Jan-Mar due to missing customers over this period.
Note on E27: Forsyth, Grant: Avg. of Jan-Mar due to missing customers over this period.
Note on O27: Forsyth, Grant: Avg. of Jan-Mar due to missing customers over this period.
Note on Q27: Forsyth, Grant: Avg. of Jan-Mar due to missing customers over this period.
Note on G32: Forsyth, Grant: Depature of Triumph to schedule 21.
Note on F188: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Change from previous method, where residential base year peak was taken from EE study. Using residential load factor to back into peak instead.
Note on F197: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Need res CTs here
Note on L231: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Average of forecasted years
Note on B239: Fuong Nguyen: KEMA System Load Research Project, Tables 29, 32, 35 KK: added "Pumping" from tables 25 and 41